## Cover
Irish TIMES Energy System Model
Document type: | Base Year Template
Sector: | Electricity generation sector (ELC)
Developer: | Energy Policy Modelling Group, UCC
Source data: | Eirgrid
CER 2012 Backcast Model
SEAI
IWEA

## Intro
Table of contents
Sheet | Description
ELC-CHP_Generators | Detailed generation portfolio
BY-Generation | TIMES detailed generation portfolio
ELC_FuelTech | TIMES fuel sectoral technologies for the power sector
Commodities | TIMES commodities for the power sector
Emi | Emission coefficients for the power sector
EB2012 | SEAI 2012 energy balance in ktoe
Wind IWEA | Detailed Wind farm capacity
Tab colour legend
VEDA Input Tables
Original data and elaboration for the TIMES tables
Units
Capacity | GW
Consumption | PJ
Currency (year) | Milion Euro 2012
Base year | 2012

## ELC-CHP_Generators
ELC - Base Year Generation Information
Source: Eirgrid Capacity Statement 2015 & 2012-13 Validated SEM Generator Data Parameters
[6 empty] | Start fuels | [7 empty] | Capacity factors |  |  |  | Ramp Rates |  |  |  | Start up Energy |  |  | Boundary times |  |  |  |  | 2012 Capacity & retirement profile
Unit ID | Unit Name | Plant type | Technology |  | Voltage | Fuel 1 | % | Fuel 2 | % | Fuel for Generation and No Load | Min Stable Capacity | Max capacity | Average Heat Rate | 2012 | Long Term Max | Forced Outage Rate | Mean Time to Repair | Up | Down | Min Up Time | Min Down Time | Cold | Warm | Hot | Hot to Warm | Warm to Cold | Commissioned Year | Projected Life | Decommissioned Year | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | LimType | CTSLvl | PeakTS | Ctype
[5 empty] | kV | [5 empty] | MW | MW | GJ/MWh | % | % | % | hrs | MW/min | MW/min | hrs | hrs | GJ | GJ | GJ | hrs | hrs | bar: 2012 Capacity & retirement profile 2012 to 2012 Capacity & retirement profile 2050
SK3 | Sealrock 3 (Aughinish CHP) | CHP | Open cycle gas turbine | OCGT | 110 | Gas | 100% |  |  | Gas | 40 | 81 | 6.3634 | 64.02% | 93% | 1.5% | 15 | 6 | 6 | 4 | 4 | 1200 | 1000 | 800 | 8 | 24 | 2005 | 35 | 2040 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SK4 | Sealrock 4 (Aughinish CHP) | CHP | Open cycle gas turbine | OCGT | 110 | Gas | 100% |  |  | Gas | 40 | 81 | 6.3378 | 65.39% | 93% | 1.5% | 15 | 6 | 6 | 4 | 4 | 1200 | 1000 | 800 | 8 | 24 | 2005 | 35 | 2040 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ED1 | Edenderry | PP | Steam turbine | ST | 110 | Oil | 100% |  |  | Peat/Biomass | 41 | 117.6 | 9.7082 | 76.3% | 90% | 5% | 72 | 1.76 | 1.76 | 4 | 0.5 | 2308 | 1084 | 436 | 4 | 48 | 2000 | 35 | 2035 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AA1 | Ardnacrusha Unit 1 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 11.9 | 21 | 3.6 | 39.53% | 44.53% | 1.463% | 60 | 0.42293 | 0.42293 | 0 | 0.25 |  |  |  | 12 | 48 | 1929 | 150 | 2079 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
AA2 | Ardnacrusha Unit 2 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 11.9 | 22 | 3.6 | 39.64% | 44.64% | 1.463% | 60 | 0.4658 | 0.4658 | 0 | 0.25 |  |  |  | 12 | 48 | 1929 | 150 | 2079 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
AA3 | Ardnacrusha Unit 3 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 11.9 | 19 | 3.6 | 39.22% | 44.22% | 1.463% | 60 | 0.33517 | 0.33517 | 0 | 0.25 |  |  |  | 12 | 48 | 1929 | 150 | 2079 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
AA4 | Ardnacrusha Unit 4 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 11.9 | 24 | 3.6 | 39.79% | 44.79% | 1.434% | 60 | 0.54958 | 0.54958 | 0 | 0.25 |  |  |  | 12 | 48 | 1929 | 150 | 2079 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
AD1 | Aghada Unit 1 | PP | Steam turbine | ST | 220 | Gas | 100% |  |  | Gas | 36 | 258 | 9.2299 | 0% | 95% | 4% | 50 | 3.8709 | 3.8709 | 4 | 3.5 | 4302 | 2185 | 1273 | 5 | 67 | 1980 | 44 | 2024 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AT1 | Aghada CT Unit 1 | PP | Open cycle gas turbine | OCGT | 220 | Gas | 100% |  |  | Gas | 15 | 90 | 12.8204 | 0% | 95% | 1.5% | 50 | 5 | 5 | 0 | 0.75 | 63 | 63 | 63 | 12 | 48 | 1980 | 44 | 2024 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AT2 | Aghada CT Unit 2 | PP | Open cycle gas turbine | OCGT | 220 | Gas | 100% |  |  | Gas | 15 | 90 | 12.7424 | 0% | 95% | 1.5% | 50 | 5 | 5 | 0 | 0.75 | 63 | 63 | 63 | 12 | 48 | 1980 | 44 | 2024 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AT4 | Aghada CT Unit 4 | PP | Open cycle gas turbine | OCGT | 220 | Gas | 100% |  |  | Gas | 15 | 90 | 12.8884 | 0% | 95% | 1.5% | 50 | 5 | 5 | 0 | 0.75 | 63 | 63 | 63 | 12 | 48 | 1980 | 44 | 2024 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DAYNITE
ER1 | Erne Unit 1 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 4 | 10 | 3.6 | 41.81% | 46.81% | 1.463% | 60 | 5 | 10 | 0 | 0.167 |  |  |  | 12 | 48 | 1950 | 150 | 2100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | SEASON
ER2 | Erne Unit 2 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 4 | 10 | 3.6 | 38.28% | 43.28% | 1.463% | 60 | 5 | 10 | 0 | 0.167 |  |  |  | 12 | 48 | 1950 | 150 | 2100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ER3 | Erne Unit 3 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 5 | 22.5 | 3.6 | 41.77% | 46.77% | 1.402% | 60 | 10 | 22.5 | 0 | 0.167 |  |  |  | 12 | 48 | 1950 | 150 | 2100 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
ER4 | Erne Unit 4 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 5 | 22.5 | 3.6 | 35.21% | 40.21% | 1.459% | 60 | 10 | 22.5 | 0 | 0.167 |  |  |  | 12 | 48 | 1950 | 150 | 2100 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
GI1 | Great Island Unit 1 | PP | Steam turbine | ST | 220 | Oil | 61% | Distillate | 39% | Oil | 24 | 54 | 14.876 | 0% | 95% | 3% | 50 | 0.7 | 1 | 4 | 2 | 562 | 449 | 218 | 12 | 48 | 1967 | 47 | 2014 | 54 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GI2 | Great Island Unit 2 | PP | Steam turbine | ST | 220 | Oil | 61% | Distillate | 39% | Oil | 24 | 49 | 15.0128 | 0% | 95% | 3% | 50 | 0.7 | 1 | 4 | 2 | 562 | 449 | 217.5 | 12 | 48 | 1967 | 47 | 2014 | 49 | 49 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GI3 | Great Island Unit 3 | PP | Steam turbine | ST | 220 | Oil | 61% | Distillate | 39% | Oil | 30 | 109 | 12.2464 | 0% | 95% | 3% | 50 | 0.7 | 1.5 | 4 | 4 | 743 | 600 | 293 | 12 | 60 | 1967 | 47 | 2014 | 109 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LE1 | Lee Unit 1 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 3 | 15 | 3.6 | 26.6% | 33% | 1.379% | 60 | 2.4 | 15 | 0 | 0.167 |  |  |  | 12 | 48 | 1957 | 150 | 2107 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LE2 | Lee Unit 2 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 1 | 4 | 3.6 | 27.74% | 33% | 1.408% | 60 | 0.6 | 4 | 0 | 0.167 |  |  |  | 12 | 48 | 1957 | 150 | 2107 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
LE3 | Lee Unit 3 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 3 | 8 | 3.6 | 27.31% | 33% | 1.379% | 60 | 1.5 | 8 | 0 | 0.167 |  |  |  | 12 | 48 | 1957 | 150 | 2107 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
LI1 | Liffey Unit 1 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 3 | 15 | 3.6 | 5.511% | 10.51% | 1.496% | 60 | 5 | 10 | 0 | 0.2 |  |  |  | 12 | 48 | 1938 | 150 | 2088 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LI2 | Liffey Unit 2 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 3 | 15 | 3.6 | 5.378% | 10.38% | 1.496% | 60 | 5 | 10 | 0 | 0.2 |  |  |  | 12 | 48 | 1938 | 150 | 2088 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
LI4 | Liffey Unit 4 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 3.99 | 4 | 3.6 | 5.583% | 10.58% | 1.496% | 60 | 2 | 2 | 0.25 | 0.133 |  |  |  | 12 | 48 | 1938 | 150 | 2088 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
LI5 | Liffey Unit 5 | PP | Hydro | HYD | 110 | Hydro | 100% |  |  | Hydro | 0.2 | 4 | 3.6 | 5.623% | 10.62% | 1.467% | 60 | 0.03 | 2 | 0 | 0.117 |  |  |  | 12 | 48 | 1938 | 150 | 2088 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
LR4 | Lough Ree Power | PP | Steam turbine | ST | 110 | Peat | 100% |  |  | Peat | 73 | 91 | 9.674 | 80.76% | 90% | 5% | 50 | 1.37 | 1.37 | 4 | 4 | 500 | 400 | 300 | 12 | 48 | 2004 | 35 | 2039 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP1 | Moneypoint Unit 1 FGD SCR | PP | Steam turbine | ST | 380 | Coal | 68% | Distillate | 32% | Coal | 99 | 285 | 9.58 | 60.86% | 90% | 4% | 50 | 1.6316 | 4.5421 | 6 | 5 | 14620 | 6920 | 4360 | 12 | 60 | 1987 | 40 | 2027 | 282 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP2 | Moneypoint Unit 2 FGD SCR | PP | Steam turbine | ST | 380 | Coal | 68% | Distillate | 32% | Coal | 99 | 285 | 9.58 | 61.12% | 90% | 4% | 50 | 1.6316 | 4.5421 | 6 | 5 | 14620 | 6920 | 4360 | 12 | 60 | 1987 | 40 | 2027 | 283 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MP3 | Moneypoint Unit 3 FGD SCR | PP | Steam turbine | ST | 380 | Coal | 68% | Distillate | 32% | Coal | 99 | 285 | 9.58 | 59.53% | 90% | 4% | 50 | 1.6316 | 4.5421 | 6 | 5 | 14620 | 6920 | 4360 | 12 | 60 | 1987 | 40 | 2027 | 282 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MRC | Marina No ST | PP | Open cycle gas turbine | OCGT | 110 | Gas | 100% |  |  | Gas | 20 | 88 | 12.8458 | 0% | 95% | 2% | 50 | 5 | 5 | 4 | 1 | 63 | 63 | 63 | 12 | 28 | 1954 | 70 | 2024 | 85 | 88 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NW5 | Northwall Unit 5 | PP | Open cycle gas turbine | OCGT | 220 | Gas | 100% |  |  | Gas | 4.01 | 104 | 13.4743 | 0% | 95% | 2% | 50 | 8 | 8 | 0 | 0.5 | 50 | 50 | 50 | 12 | 48 | 2012 | 30 | 2042 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PBC | Poolbeg Combined Cycle | PP | Open cycle gas turbine | OCGT | 220 | Gas | 100% |  |  | Gas | 232 | 463 | 7.3313 | 33.08% | 95% | 3% | 50 | 11 | 11 | 4 | 4 | 2800 | 1800 | 1500 | 8 | 112 | 2000 | 30 | 2030 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RH1 | Rhode 1 | PP | Open cycle gas turbine | OCGT | 110 | Distillate | 100% |  |  | Distillate | 12 | 52 | 11.7882 | 0% | 95% | 3% | 50 | 5 | 10 | 0 | 0.75 | 24 | 24 | 24 | 12 | 60 | 2004 | 30 | 2034 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RH2 | Rhode 2 | PP | Open cycle gas turbine | OCGT | 110 | Distillate | 100% |  |  | Distillate | 12 | 52 | 11.7718 | 0% | 95% | 3% | 50 | 5 | 10 | 0 | 0.75 | 24 | 24 | 24 | 12 | 60 | 2004 | 30 | 2034 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TB1 | Tarbert Unit 1 | PP | Steam turbine | ST | 110 | Oil | 61% | Distillate | 39% | Oil | 20 | 54 | 12.6042 | 0% | 95% | 3% | 50 | 1 | 1 | 2 | 2 | 562 | 449 | 217.5 | 12 | 60 | 1969 | 53 | 2022 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TB2 | Tarbert Unit 2 | PP | Steam turbine | ST | 110 | Oil | 61% | Distillate | 39% | Oil | 20 | 54 | 12.6028 | 0% | 95% | 3% | 50 | 1 | 1 | 2 | 2 | 562 | 449 | 217.5 | 12 | 60 | 1969 | 53 | 2022 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TB3 | Tarbert Unit 3 | PP | Steam turbine | ST | 220 | Oil | 70% | Distillate | 30% | Oil | 34.85 | 243 | 10.7008 | 0% | 95% | 3% | 50 | 1.7 | 2.2 | 24 | 4 | 3180 | 1934 | 1072 | 14 | 120 | 1969 | 53 | 2022 | 243 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TB4 | Tarbert Unit 4 | PP | Steam turbine | ST | 220 | Oil | 70% | Distillate | 30% | Oil | 34.85 | 243 | 11.0493 | 0% | 95% | 3% | 50 | 1.7 | 2.2 | 24 | 4 | 3180 | 1934 | 1072 | 14 | 120 | 1969 | 53 | 2022 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TH1 | Turlough Hill Unit 1 | ST | Pumped Storage |  | 220 | Pumped Storage | 100% |  |  | Pumped Storage | 5 | 73 | 4.8 | 11.56% | 16.56% | 0.9768% | 60 | 210 | 270 | 0 | 0 |  |  |  | 12 | 48 | 1974 | 150 | 2124 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
TH2 | Turlough Hill Unit 2 | ST | Pumped Storage |  | 220 | Pumped Storage | 100% |  |  | Pumped Storage | 5 | 73 | 4.8 | 11.37% | 16.37% | 1.954% | 60 | 210 | 270 | 0 | 0 |  |  |  | 12 | 48 | 1974 | 150 | 2124 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
TH3 | Turlough Hill Unit 3 | ST | Pumped Storage |  | 220 | Pumped Storage | 100% |  |  | Pumped Storage | 5 | 73 | 4.8 | 10.7% | 15.7% | 1.954% | 60 | 210 | 270 | 0 | 0 |  |  |  | 12 | 48 | 1974 | 150 | 2124 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
TH4 | Turlough Hill Unit 4 | ST | Pumped Storage |  | 220 | Pumped Storage | 100% |  |  | Pumped Storage | 5 | 73 | 4.8 | 10.46% | 15.46% | 0.6803% | 60 | 210 | 270 | 0 | 0 |  |  |  | 12 | 48 | 1974 | 150 | 2124 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
TP1 | Tawnaghmore 1 | PP | Open cycle gas turbine | OCGT | 110 | Distillate | 100% |  |  | Distillate | 12 | 52 | 11.6676 | 0% | 95% | 3% | 50 | 5 | 10 | 0 | 0.75 | 24 | 24 | 24 | 12 | 60 | 2003 | 30 | 2033 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WO4 | West Offaly Power | PP | Steam turbine | ST | 110 | Peat | 100% |  |  | Peat | 47.64 | 137 | 8.52 | 76.84% | 90% | 5% | 50 | 0.7 | 0.7 | 4 | 4 | 750 | 600 | 450 | 12 | 60 | 2005 | 30 | 2035 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DB1 | Dublin Bay Power | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 209 | 415 | 6.8327 | 35.32% | 90% | 2% | 48 | 10 | 9 | 4 | 4 | 7700 | 2603.6 | 2600 | 12 | 60 | 2002 | 30 | 2032 | 403 | 405 | 404 | 403 | 402 | 405 | 404 | 403 | 402 | 405 | 404 | 403 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TY | Tynagh | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 194 | 388.475 | 6.7324 | 62.95% | 90% | 3.6% | 55 | 12.5 | 12.5 | 4 | 4 | 5033 | 2944 | 2017 | 12 | 48 | 2006 | 30 | 2036 | 384 | 387 | 387 | 386 | 386 | 386 | 386 | 386 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HN2 | Huntstown Phase II | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 170 | 404 | 6.7304 | 50.69% | 90% | 7% | 55 | 20 | 20 | 4 | 4 | 644.171 | 531.129 | 318.454 | 12 | 60 | 2007 | 30 | 2037 | 399 | 399 | 398 | 398 | 397 | 397 | 396 | 396 | 395 | 395 | 394 | 394 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HNC | Huntstown | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 171 | 343 | 6.7656 | 23.72% | 90% | 7% | 55 | 7 | 7 | 4 | 4 | 4771.682 | 2803.196 | 834.687 | 12 | 60 | 2002 | 30 | 2032 | 341 | 341 | 340 | 340 | 339 | 339 | 338 | 338 | 337 | 337 | 336 | 336 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ADC | Aghada CCGT | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 215.8 | 431.6 | 6.2359 | 60.94% | 90% | 3% | 50 | 9.241 | 12.43 | 4 | 0 | 2400 | 1800 | 1200 | 12 | 60 | 2010 | 30 | 2040 | 432 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WG | Whitegate | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 180 | 445 | 6.6154 | 64.72% | 90% | 3.35% | 32.14 | 20 | 20 | 4 | 0 | 437.1273 | 329.8658 | 222.6042 | 12 | 72 | 2010 | 30 | 2040 | 439 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ED3 | Cushaling | PP | Open Cycle | OCGT | 110 | Distillate | 100% |  |  | Distillate | 20 | 58 | 11.4074 | 0% | 95% | 2% | 24 | 5 | 5 | 0 | 0.08 | 20 | 20 | 20 | 0.5 | 1 | 2010 | 30 | 2040 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ED5 | Cushaling | PP | Open Cycle | OCGT | 110 | Distillate | 100% |  |  | Distillate | 20 | 58 | 11.399 | 0% | 95% | 2% | 24 | 5 | 5 | 0 | 0.08 | 20 | 20 | 20 | 0.5 | 1 | 2010 | 30 | 2040 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TP3 | Tawnaghmore 3 | PP | Open Cycle | OCGT | 110 | Distillate | 100% |  |  | Distillate | 12 | 52 | 11.6101 | 0% | 95% | 3% | 50 | 5 | 10 | 0 | 0.75 | 24 | 24 | 24 | 12 | 60 | 2003 | 30 | 2033 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meath | Meath Waste-to-Energy | PP | Steam turbine | ST | 110 | Waste |  |  |  | Waste | 0 | 16 | 10.2 | 80.53% | 90% | 1.918% | 24 | 1.38 | 1.5 | 1.33 | 1.33 | [5 empty] | 2011 | 25 | 2036 | 15 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GI4 | Great Island CCGT | PP | Combined cycle gas turbine | CCGT | 220 | Gas | 100% |  |  | Gas | 230 | 461 | 6.24 | 0% | 90% | 3% | 55 | 12 | 15 | 4 | 4 | 2400 | 1800 | 1200 | 12 | 60 | 2015 | 30 | 2045 | 0 | 0 | 0 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 0 | 0 | 0 | 0 | 0
WindROI | WindROI | PP | Wind |  | 110 | Wind | 100% |  |  | Wind | 0 | 1642 | 3.6 | 28.5% | 30% | [11 empty] | - | 25 | - | 1642 | 1642 | 1642 | 1642 | 1642 | 1635.55 | 1635.55 | 1635.55 | 1635.55 | 1635.55 | 1584.77 | 1579.77 | 1571.19 | 1526.82 | 1523.42 | 1511.52 | 1446.41 | 1295.36 | 1134.42 | 995.37 | 896.52 | 677.69 | 358.32 | 244 | 15.31
Biomass CHP | Biomass CHP | CHP | Biomass CHP |  | 110 | Biomass | 100% |  |  | Biomass | 0 | 45 | 10.2 | 60% | 60% | [12 empty] | 35
Northern Ireland
B10 | Ballylumford Unit 10 |  |  |  |  | Gas | 100% |  |  | Gas | 63 | 101 | 6.9947 | 47.7% | 90% | 5% | 72 | 1.06 | 3.98 | 0.02 | 0.25 | 405 | 225 | 135 | 8 | 40 | B9 |  |  | 2012 Capacity & retirement profile 2013: 97; 2012 Capacity & retirement profile 2014: 97; 2012 Capacity & retirement profile 2015: 97; 2012 Capacity & retirement profile 2016: 97; 2012 Capacity & retirement profile 2017: 97; 2012 Capacity & retirement profile 2018: 97; 2012 Capacity & retirement profile 2019: 97; 2012 Capacity & retirement profile 2020: 97; 2012 Capacity & retirement profile 2021: 97; 2012 Capacity & retirement profile 2022: 97; 2012 Capacity & retirement profile 2023: 97; 2012 Capacity & retirement profile 2024: 97
B31 | Ballylumford Unit 31 |  |  |  |  | Gas | 100% |  |  | Gas | 113 | 247 | 7.2233 | 34.17% | 90% | 3% | 72 | 3.1 | 10.7 | 0.02 | 0.25 | 2025 | 1134 | 639 | 8 | 40 | B30 |  |  | 2012 Capacity & retirement profile 2013: 245; 2012 Capacity & retirement profile 2014: 245; 2012 Capacity & retirement profile 2015: 245; 2012 Capacity & retirement profile 2016: 245; 2012 Capacity & retirement profile 2017: 245; 2012 Capacity & retirement profile 2018: 245; 2012 Capacity & retirement profile 2019: 245; 2012 Capacity & retirement profile 2020: 245; 2012 Capacity & retirement profile 2021: 245; 2012 Capacity & retirement profile 2022: 245; 2012 Capacity & retirement profile 2023: 245; 2012 Capacity & retirement profile 2024: 245
B32 | Ballylumford Unit 32 |  |  |  |  | Gas | 100% |  |  | Gas | 113 | 247 | 7.2412 | 34.32% | 90% | 3% | 72 | 3.1 | 10.7 | 0.02 | 0.25 | 2025 | 1134 | 639 | 8 | 40 | B31 |  |  | 2012 Capacity & retirement profile 2013: 245; 2012 Capacity & retirement profile 2014: 245; 2012 Capacity & retirement profile 2015: 245; 2012 Capacity & retirement profile 2016: 245; 2012 Capacity & retirement profile 2017: 245; 2012 Capacity & retirement profile 2018: 245; 2012 Capacity & retirement profile 2019: 245; 2012 Capacity & retirement profile 2020: 245; 2012 Capacity & retirement profile 2021: 245; 2012 Capacity & retirement profile 2022: 245; 2012 Capacity & retirement profile 2023: 245; 2012 Capacity & retirement profile 2024: 245
B4 | Ballylumford Unit 4 |  |  |  |  | Gas | 100% |  |  | Gas | 54 | 170 | 12.087 | 0% | 95% | 11% | 72 | 1.98 | 9.67 | 0.02 | 0.02 | 2070 | 1530 | 810 | 10 | 26 | B3 |  |  | 2012 Capacity & retirement profile 2013: 170; 2012 Capacity & retirement profile 2014: 170; 2012 Capacity & retirement profile 2015: 170; 2012 Capacity & retirement profile 2016: 0; 2012 Capacity & retirement profile 2017: 0; 2012 Capacity & retirement profile 2018: 0; 2012 Capacity & retirement profile 2019: 0; 2012 Capacity & retirement profile 2020: 0; 2012 Capacity & retirement profile 2021: 0; 2012 Capacity & retirement profile 2022: 0; 2012 Capacity & retirement profile 2023: 0; 2012 Capacity & retirement profile 2024: 0
B6 | Ballylumford Unit 6 |  |  |  |  | Gas | 100% |  |  | Gas | 54 | 170 | 11.2572 | 0% | 95% | 5% | 72 | 1.98 | 9.76 | 0.02 | 0.02 | 2070 | 1530 | 810 | 10 | 26 | B5 |  |  | 2012 Capacity & retirement profile 2013: 170; 2012 Capacity & retirement profile 2014: 170; 2012 Capacity & retirement profile 2015: 170; 2012 Capacity & retirement profile 2016: 0; 2012 Capacity & retirement profile 2017: 0; 2012 Capacity & retirement profile 2018: 0; 2012 Capacity & retirement profile 2019: 0; 2012 Capacity & retirement profile 2020: 0; 2012 Capacity & retirement profile 2021: 0; 2012 Capacity & retirement profile 2022: 0; 2012 Capacity & retirement profile 2023: 0; 2012 Capacity & retirement profile 2024: 0
BGT1 | Ballylumford GT1 |  |  |  |  | Distillate | 100% |  |  | Distillate | 8 | 58 | 13.8253 | 0% | 95% | 2% | 72 | 10 | 18 | 0.02 | 0.25 | 7.6 | 7.6 | 7.6 | n/a = OCGT | 0 | BGT0 |  |  | 2012 Capacity & retirement profile 2013: 58; 2012 Capacity & retirement profile 2014: 58; 2012 Capacity & retirement profile 2015: 58; 2012 Capacity & retirement profile 2016: 58; 2012 Capacity & retirement profile 2017: 58; 2012 Capacity & retirement profile 2018: 58; 2012 Capacity & retirement profile 2019: 58; 2012 Capacity & retirement profile 2020: 58; 2012 Capacity & retirement profile 2021: 58; 2012 Capacity & retirement profile 2022: 58; 2012 Capacity & retirement profile 2023: 58; 2012 Capacity & retirement profile 2024: 58
BGT2 | Ballylumford GT2 |  |  |  |  | Distillate | 100% |  |  | Distillate | 8 | 58 | 13.8507 | 0% | 95% | 2% | 72 | 10 | 18 | 0.02 | 0.25 | 7.6 | 7.6 | 7.6 | n/a = OCGT | 0 | BGT1 |  |  | 2012 Capacity & retirement profile 2013: 58; 2012 Capacity & retirement profile 2014: 58; 2012 Capacity & retirement profile 2015: 58; 2012 Capacity & retirement profile 2016: 58; 2012 Capacity & retirement profile 2017: 58; 2012 Capacity & retirement profile 2018: 58; 2012 Capacity & retirement profile 2019: 58; 2012 Capacity & retirement profile 2020: 58; 2012 Capacity & retirement profile 2021: 58; 2012 Capacity & retirement profile 2022: 58; 2012 Capacity & retirement profile 2023: 58; 2012 Capacity & retirement profile 2024: 58
B5 | Ballylumford Unit 5 |  |  |  |  | Gas | 100% |  |  | Gas | 54 | 170 | 12.445 | 0% | 95% | 3% | 72 | 1.98 | 9.76 | 0.02 | 0.02 | 2070 | 1530 | 810 | 10 | 26 | B4 |  |  | 2012 Capacity & retirement profile 2013: 170; 2012 Capacity & retirement profile 2014: 170; 2012 Capacity & retirement profile 2015: 170; 2012 Capacity & retirement profile 2016: 0; 2012 Capacity & retirement profile 2017: 0; 2012 Capacity & retirement profile 2018: 0; 2012 Capacity & retirement profile 2019: 0; 2012 Capacity & retirement profile 2020: 0; 2012 Capacity & retirement profile 2021: 0; 2012 Capacity & retirement profile 2022: 0; 2012 Capacity & retirement profile 2023: 0; 2012 Capacity & retirement profile 2024: 0
K1 Coal 220 | Kilroot Unit 1 FGD |  |  |  |  | Coal | 60% | Oil | 40% | Coal | 93 | 238 | 12.9217 | 45.86% | 90% | 3.2% | 72 | 5.79 | 5.79 | 4 | 0.5 | 6827 | 4727 | 2947 | 10 | 55 | K1 Coal 219 |  |  | 2012 Capacity & retirement profile 2013: 238; 2012 Capacity & retirement profile 2014: 238; 2012 Capacity & retirement profile 2015: 238; 2012 Capacity & retirement profile 2016: 238; 2012 Capacity & retirement profile 2017: 238; 2012 Capacity & retirement profile 2018: 238; 2012 Capacity & retirement profile 2019: 238; 2012 Capacity & retirement profile 2020: 238; 2012 Capacity & retirement profile 2021: 238; 2012 Capacity & retirement profile 2022: 238; 2012 Capacity & retirement profile 2023: 238; 2012 Capacity & retirement profile 2024: 0
K2 Coal 220 | Kilroot Unit 2 FGD |  |  |  |  | Coal | 60% | Oil | 40% | Coal | 93 | 238 | 12.8435 | 45.18% | 90% | 3.2% | 72 | 5.79 | 5.79 | 4 | 0.5 | 6827 | 4727 | 2947 | 10 | 55 | K2 Coal 219 |  |  | 2012 Capacity & retirement profile 2013: 238; 2012 Capacity & retirement profile 2014: 238; 2012 Capacity & retirement profile 2015: 238; 2012 Capacity & retirement profile 2016: 238; 2012 Capacity & retirement profile 2017: 238; 2012 Capacity & retirement profile 2018: 238; 2012 Capacity & retirement profile 2019: 238; 2012 Capacity & retirement profile 2020: 238; 2012 Capacity & retirement profile 2021: 238; 2012 Capacity & retirement profile 2022: 238; 2012 Capacity & retirement profile 2023: 238; 2012 Capacity & retirement profile 2024: 0
KGT1 | Kilroot GT1 |  |  |  |  | Distillate | 100% |  |  | Distillate | 5.4 | 29 | 14.0334 | 0% | 95% | 0.8219% | 72 | 6 | 6 | 0.33 | 0.25 | 7.6 | 7.6 | 7.6 | n/a = OCGT | 0 | KGT0 |  |  | 2012 Capacity & retirement profile 2013: 29; 2012 Capacity & retirement profile 2014: 29; 2012 Capacity & retirement profile 2015: 29; 2012 Capacity & retirement profile 2016: 29; 2012 Capacity & retirement profile 2017: 29; 2012 Capacity & retirement profile 2018: 29; 2012 Capacity & retirement profile 2019: 29; 2012 Capacity & retirement profile 2020: 29; 2012 Capacity & retirement profile 2021: 29; 2012 Capacity & retirement profile 2022: 29; 2012 Capacity & retirement profile 2023: 29; 2012 Capacity & retirement profile 2024: 29
KGT2 | Kilroot GT2 |  |  |  |  | Distillate | 100% |  |  | Distillate | 5.4 | 29 | 13.8579 | 0% | 95% | 0.8219% | 72 | 6 | 6 | 0.33 | 0.25 | 7.6 | 7.6 | 7.6 | n/a = OCGT | 0 | KGT1 |  |  | 2012 Capacity & retirement profile 2013: 29; 2012 Capacity & retirement profile 2014: 29; 2012 Capacity & retirement profile 2015: 29; 2012 Capacity & retirement profile 2016: 29; 2012 Capacity & retirement profile 2017: 29; 2012 Capacity & retirement profile 2018: 29; 2012 Capacity & retirement profile 2019: 29; 2012 Capacity & retirement profile 2020: 29; 2012 Capacity & retirement profile 2021: 29; 2012 Capacity & retirement profile 2022: 29; 2012 Capacity & retirement profile 2023: 29; 2012 Capacity & retirement profile 2024: 29
KGT3 | Kilroot GT3 |  |  |  |  | Distillate | 100% |  |  | Distillate | 12.8194 | 42 | 12.4966 | 0% | 95% | 2% | 72 | 10 | 10 | 0.33 | 0.38 | 9.55 | 9.55 | 9.55 | n/a = OCGT | 0 | KGT2 |  |  | 2012 Capacity & retirement profile 2013: 42; 2012 Capacity & retirement profile 2014: 42; 2012 Capacity & retirement profile 2015: 42; 2012 Capacity & retirement profile 2016: 42; 2012 Capacity & retirement profile 2017: 42; 2012 Capacity & retirement profile 2018: 42; 2012 Capacity & retirement profile 2019: 42; 2012 Capacity & retirement profile 2020: 42; 2012 Capacity & retirement profile 2021: 42; 2012 Capacity & retirement profile 2022: 42; 2012 Capacity & retirement profile 2023: 42; 2012 Capacity & retirement profile 2024: 42
KGT4 | Kilroot GT4 |  |  |  |  | Distillate | 100% |  |  | Distillate | 12.8194 | 42 | 12.31 | 0% | 95% | 2% | 72 | 10 | 10 | 0.33 | 0.38 | 9.55 | 9.55 | 9.55 | n/a = OCGT | 0 | KGT3 |  |  | 2012 Capacity & retirement profile 2013: 42; 2012 Capacity & retirement profile 2014: 42; 2012 Capacity & retirement profile 2015: 42; 2012 Capacity & retirement profile 2016: 42; 2012 Capacity & retirement profile 2017: 42; 2012 Capacity & retirement profile 2018: 42; 2012 Capacity & retirement profile 2019: 42; 2012 Capacity & retirement profile 2020: 42; 2012 Capacity & retirement profile 2021: 42; 2012 Capacity & retirement profile 2022: 42; 2012 Capacity & retirement profile 2023: 42; 2012 Capacity & retirement profile 2024: 42
CGT8 | Coolkeeragh GT8 |  |  |  |  | Distillate | 100% |  |  | Distillate | 8 | 58 | 14.0792 | 0% | 95% | 1.096% | 72 | 10 | 10 | 0.02 | 0.25 | 8 | 8 | 8 | n/a = OCGT | 0 | CGT7 |  |  | 2012 Capacity & retirement profile 2013: 58; 2012 Capacity & retirement profile 2014: 53; 2012 Capacity & retirement profile 2015: 53; 2012 Capacity & retirement profile 2016: 53; 2012 Capacity & retirement profile 2017: 53; 2012 Capacity & retirement profile 2018: 53; 2012 Capacity & retirement profile 2019: 53; 2012 Capacity & retirement profile 2020: 53; 2012 Capacity & retirement profile 2021: 53; 2012 Capacity & retirement profile 2022: 53; 2012 Capacity & retirement profile 2023: 53; 2012 Capacity & retirement profile 2024: 53
CPS CCGT | Coolkeeragh CCGT |  |  |  |  | Gas | 100% |  |  | Gas | 260 | 404 | 6.3731 | 47.33% | 90% | 2% | 72 | 15 | 18.5 | 4 | 4 | 5257 | 3046 | 1088 | 8 | 36 | CPS CCGT |  |  | 2012 Capacity & retirement profile 2013: 402; 2012 Capacity & retirement profile 2014: 402; 2012 Capacity & retirement profile 2015: 402; 2012 Capacity & retirement profile 2016: 402; 2012 Capacity & retirement profile 2017: 402; 2012 Capacity & retirement profile 2018: 402; 2012 Capacity & retirement profile 2019: 402; 2012 Capacity & retirement profile 2020: 402; 2012 Capacity & retirement profile 2021: 402; 2012 Capacity & retirement profile 2022: 402; 2012 Capacity & retirement profile 2023: 402; 2012 Capacity & retirement profile 2024: 402
Contour 1 | Contour Global unit 1 |  |  |  |  | Gas | 100% |  |  | Gas | 2 | 3.021 | 8.1717 | 10.15% | 90% | 4% | 60 | 1.008 | 1.008 | 1 | 1 | 0 | 0 | 0 | 0.25 | 0.25 | Contour 0 |  |  | 2012 Capacity & retirement profile 2013: 3; 2012 Capacity & retirement profile 2014: 4; 2012 Capacity & retirement profile 2015: 4; 2012 Capacity & retirement profile 2016: 4; 2012 Capacity & retirement profile 2017: 6; 2012 Capacity & retirement profile 2018: 6; 2012 Capacity & retirement profile 2019: 6; 2012 Capacity & retirement profile 2020: 6; 2012 Capacity & retirement profile 2021: 6; 2012 Capacity & retirement profile 2022: 6; 2012 Capacity & retirement profile 2023: 6; 2012 Capacity & retirement profile 2024: 6
Contour 2 | Contour Global unit 2 |  |  |  |  | Gas | 100% |  |  | Gas | 2 | 3.021 | 8.17 | 10.34% | 90% | 4% | 60 | 1.008 | 1.008 | 1 | 1 | 0 | 0 | 0 | 0.25 | 0.25 | Contour 1 |  |  | 2012 Capacity & retirement profile 2013: 3; 2012 Capacity & retirement profile 2014: 4; 2012 Capacity & retirement profile 2015: 4; 2012 Capacity & retirement profile 2016: 4; 2012 Capacity & retirement profile 2017: 6; 2012 Capacity & retirement profile 2018: 6; 2012 Capacity & retirement profile 2019: 6; 2012 Capacity & retirement profile 2020: 6; 2012 Capacity & retirement profile 2021: 6; 2012 Capacity & retirement profile 2022: 6; 2012 Capacity & retirement profile 2023: 6; 2012 Capacity & retirement profile 2024: 6
Contour 3 | Contour Global unit 3 |  |  |  |  | Gas | 100% |  |  | Gas | 2 | 3.021 | 8.17 | 10.32% | 90% | 4% | 60 | 1.008 | 1.008 | 1 | 1 | 0 | 0 | 0 | 0.25 | 0.25 | Contour 2 |  |  | 2012 Capacity & retirement profile 2013: 3; 2012 Capacity & retirement profile 2014: 4; 2012 Capacity & retirement profile 2015: 4; 2012 Capacity & retirement profile 2016: 4; 2012 Capacity & retirement profile 2017: 6; 2012 Capacity & retirement profile 2018: 6; 2012 Capacity & retirement profile 2019: 6; 2012 Capacity & retirement profile 2020: 6; 2012 Capacity & retirement profile 2021: 6; 2012 Capacity & retirement profile 2022: 6; 2012 Capacity & retirement profile 2023: 6; 2012 Capacity & retirement profile 2024: 6
WindNI | WindNI |  |  |  |  | Wind | 100% |  |  | Wind | 0 | 467 | 3.6 |  | 100% | [11 empty] | Wind NI |  |  | 2012 Capacity & retirement profile 2013: 553; 2012 Capacity & retirement profile 2014: 658; 2012 Capacity & retirement profile 2015: 870; 2012 Capacity & retirement profile 2016: 975; 2012 Capacity & retirement profile 2017: 1036; 2012 Capacity & retirement profile 2018: 1094; 2012 Capacity & retirement profile 2019: 1145; 2012 Capacity & retirement profile 2020: 1205; 2012 Capacity & retirement profile 2021: 1256; 2012 Capacity & retirement profile 2022: 1297; 2012 Capacity & retirement profile 2023: 1345; 2012 Capacity & retirement profile 2024: 1389
SolarNI | SolarNI |  |  |  |  | Solar | 200% |  |  | Solar | 0 | 2 | 3.6 |  | 100% | [11 empty] | Solar NI |  |  | 2012 Capacity & retirement profile 2013: 2; 2012 Capacity & retirement profile 2014: 36; 2012 Capacity & retirement profile 2015: 48; 2012 Capacity & retirement profile 2016: 60; 2012 Capacity & retirement profile 2017: 76; 2012 Capacity & retirement profile 2018: 85; 2012 Capacity & retirement profile 2019: 92; 2012 Capacity & retirement profile 2020: 98; 2012 Capacity & retirement profile 2021: 105; 2012 Capacity & retirement profile 2022: 111; 2012 Capacity & retirement profile 2023: 116; 2012 Capacity & retirement profile 2024: 121
3
85%
Note on O4: Paul Deane: From PLEXOS CER Model 2012 results. CF are adjusted down by 5% to account for Reserve, constraints and opertational factors
Note on B6: Power to Heat ratio=0.55 should based on CER "Certification Process for High Efficiency CHP" Decision Paper"
Note on N59: Alessandro Chiodi: Estimate based on 2012 SEAI Energy Balance Reduced to 30%. Assumed eff for energy forecasts
Note on O61: Paul Deane: http://www.eirgridgroup.com/site-files/library/EirGrid/2012_Curtailment_Report.pdf in 2012 the average capacity factor was 28.5%.

## BY-Generation
Base Year Electricity Generation Plants
|  |  | ~FI_T | [20 empty] | ~FI_Process
TechName | *TechDesc | Comm-IN | Comm-OUT | EFF | AF | AF~2013 | * | Life | *Stock | Cap2Act | Share-I~UP~ELCBIO | Share-I~UP~ELCGAS | CHPR | CEH |  |  | Calibration (ELC prod) |  | Should be (EnBal) |  | Calibration (Fuel cons) |  | Should be (EnBal) | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Technology Name | Technology Description | Input Commodity | Output Commodity | Efficiency | Availability factor | Availability factor |  | Years | GW |  | Input Share | Input Share |  |  |  |  | PJ | ktoe | ktoe |  | PJ | ktoe | ktoe | *
ECHPGas_00_OCGT-SK | Existing CHP - Sealrock (Aughinish) OCGT | ELCGAS | ELCC,ELCH | 56.69% | 64.7% | 93% | 2005 | 35 | 0.162 | 31.536 |  |  | 1.8182 | 1 |  |  | 3.3056 | 78.9521 |  |  | 5.8312 | 139.276 |  | CHP | ECHPGas_00_OCGT-SK | Existing CHP - Sealrock (Aughinish) OCGT | PJ | GW | DAYNITE | ELCC
EPPPea_00_ST-ED | Existing Power Plant - Edenderry ST | ELCPEA, ELCBIO | ELCC | 37.08% | 76.3% | 90% | 2000 | 35 | 0.118 | 31.536 | 100% | [5 empty] | 2.8393 | 67.8147 |  |  | 7.6567 | 182.8783 |  | ELE | EPPPea_00_ST-ED | Existing Power Plant - Edenderry ST | PJ | GW | DAYNITE
EPPHyd_00-AA | Existing Power Plant - Ardnacrusha HYD | ELCHYD | ELCC | 100% | 39.55% | 44.55% | 1929 | 150 | 0.086 | 31.536 | [6 empty] | 1.0726 | 25.6177 |  |  | 1.0726 | 25.6177 |  |  | EPPHyd_00-AA | Existing Power Plant - Ardnacrusha HYD | PJ | GW | DAYNITE
EPPGas_00_ST-AD | Existing Power Plant - Aghada ST | ELCGAS | ELCC | 39% | 0% | 95% | 1980 | 44 | 0.258 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPGas_00_ST-AD | Existing Power Plant - Aghada ST | PJ | GW | DAYNITE
EPPGas_00_OCGT-AT | Existing Power Plant - Aghada CT OCGT | ELCGAS | ELCC | 28.09% | 0% | 95% | 1980 | 44 | 0.27 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPGas_00_OCGT-AT | Existing Power Plant - Aghada CT OCGT | PJ | GW | DAYNITE
EPPHyd_00-ER | Existing Power Plant - Erne HYD | ELCHYD | ELCC | 100% | 39.27% | 44.27% | 1950 | 150 | 0.065 | 31.536 | [6 empty] | 0.80495 | 19.2259 |  |  | 0.80495 | 19.2259 |  |  | EPPHyd_00-ER | Existing Power Plant - Erne HYD | PJ | GW | DAYNITE
EPPOil_00_ST-GI | Existing Power Plant - Great Island ST | ELCHFO | ELCC | 26.56% | 0% | 95% | 1967 | 47 | 0.212 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPOil_00_ST-GI | Existing Power Plant - Great Island ST | PJ | GW | DAYNITE
EPPHyd_00-LE | Existing Power Plant - Lee HYD | ELCHYD | ELCC | 100% | 27.21% | 33% | 1957 | 150 | 0.027 | 31.536 | [6 empty] | 0.23172 | 5.5345 |  |  | 0.23172 | 5.5345 |  |  | EPPHyd_00-LE | Existing Power Plant - Lee HYD | PJ | GW | DAYNITE
EPPHyd_00-LI | Existing Power Plant - Liffey HYD | ELCHYD | ELCC | 100% | 5.524% | 10.52% | 1938 | 150 | 0.038 | 31.536 | [6 empty] | 0.066193 | 1.581 |  |  | 0.066193 | 1.581 |  |  | EPPHyd_00-LI | Existing Power Plant - Liffey HYD | PJ | GW | DAYNITE
EPPPea_00_ST-LR | Existing Power Plant - Lough Ree Power ST | ELCPEA | ELCC | 37.21% | 80.76% | 90% | 2004 | 35 | 0.091 | 31.536 | [6 empty] | 2.3177 | 55.3583 |  |  | 6.2283 | 148.7607 |  |  | EPPPea_00_ST-LR | Existing Power Plant - Lough Ree Power ST | PJ | GW | DAYNITE
EPPCoa_00_ST-MP | Existing Power Plant - Moneypoint ST | ELCCOA | ELCC | 37.58% | 60.5% | 90% | 1987 | 40 | 0.847 | 31.536 | [6 empty] | 16.1609 | 385.9973 |  |  | 43.006 | 1027.1816 |  |  | EPPCoa_00_ST-MP | Existing Power Plant - Moneypoint ST | PJ | GW | SEASON
EPPGas_00_OCGT-MRC | Existing Power Plant - Marina No OCGT | ELCGAS | ELCC | 28.02% | 0% | 95% | 1954 | 70 | 0.085 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPGas_00_OCGT-MRC | Existing Power Plant - Marina No OCGT | PJ | GW | DAYNITE
EPPGas_00_OCGT-NW | Existing Power Plant - Northwall OCGT | ELCGAS | ELCC | 26.72% | 0% | 95% | 2012 | 30 | 0.104 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPGas_00_OCGT-NW | Existing Power Plant - Northwall OCGT | PJ | GW | DAYNITE
EPPGas_00_OCGT-PBC | Existing Power Plant - Poolbeg OCGT | ELCGAS | ELCC | 49.1% | 33.08% | 95% | 2000 | 30 | 0.463 | 31.536 | [6 empty] | 4.8304 | 115.3727 |  |  | 9.837 | 234.9539 |  |  | EPPGas_00_OCGT-PBC | Existing Power Plant - Poolbeg OCGT | PJ | GW | DAYNITE
EPPDis_00_OCGT-RH | Existing Power Plant - Rhode OCGT | ELCDIS | ELCC | 30.56% | 0% | 95% | 2004 | 30 | 0.104 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPDis_00_OCGT-RH | Existing Power Plant - Rhode OCGT | PJ | GW | DAYNITE
EPPOil_00_ST-TB | Existing Power Plant - Tarbert Unit ST | ELCHFO | ELCC | 32.17% | 0% | 95% | 1969 | 53 | 0.594 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPOil_00_ST-TB | Existing Power Plant - Tarbert Unit ST | PJ | GW | DAYNITE
EPPDis_00_OCGT-TP1 | Existing Power Plant - Tawnaghmore 1 OCGT | ELCDIS | ELCC | 30.85% | 0% | 95% | 2003 | 30 | 0.052 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPDis_00_OCGT-TP1 | Existing Power Plant - Tawnaghmore 1 OCGT | PJ | GW | DAYNITE
EPPPea_00_ST-WO | Existing Power Plant - West Offaly Power ST | ELCPEA | ELCC | 42.25% | 76.84% | 90% | 2005 | 30 | 0.137 | 31.536 | [6 empty] | 3.3196 | 79.2883 |  |  | 7.8565 | 187.6489 |  |  | EPPPea_00_ST-WO | Existing Power Plant - West Offaly Power ST | PJ | GW | DAYNITE
EPPGas_00_CCGT-DB | Existing Power Plant - Dublin Bay Power CCGT | ELCGAS | ELCC | 52.69% | 35.32% | 90% | 2002 | 30 | 0.403 | 31.536 | [6 empty] | 4.4889 | 107.2158 |  |  | 8.5198 | 203.4921 |  |  | EPPGas_00_CCGT-DB | Existing Power Plant - Dublin Bay Power CCGT | PJ | GW | DAYNITE
EPPGas_00_CCGT-TY | Existing Power Plant - Tynagh CCGT | ELCGAS | ELCC | 53.47% | 62.95% | 90% | 2006 | 30 | 0.384 | 31.536 | [6 empty] | 7.6233 | 182.0795 |  |  | 14.2563 | 340.507 |  |  | EPPGas_00_CCGT-TY | Existing Power Plant - Tynagh CCGT | PJ | GW | DAYNITE
EPPGas_00_CCGT-HN | Existing Power Plant - Huntstown Phase II CCGT | ELCGAS | ELCC | 53.49% | 50.69% | 90% | 2007 | 30 | 0.399 | 31.536 | [6 empty] | 6.3788 | 152.3559 |  |  | 11.9256 | 284.8378 |  |  | EPPGas_00_CCGT-HN | Existing Power Plant - Huntstown Phase II CCGT | PJ | GW | DAYNITE
EPPGas_00_CCGT-HNC | Existing Power Plant - Huntstown CCGT | ELCGAS | ELCC | 53.21% | 23.72% | 90% | 2002 | 30 | 0.341 | 31.536 | [6 empty] | 2.5512 | 60.9348 |  |  | 4.7946 | 114.5175 |  |  | EPPGas_00_CCGT-HNC | Existing Power Plant - Huntstown CCGT | PJ | GW | DAYNITE
EPPGas_00_CCGT-ADC | Existing Power Plant - Aghada CCGT | ELCGAS | ELCC | 57.73% | 60.94% | 90% | 2010 | 30 | 0.432 | 31.536 | [6 empty] | 8.3024 | 198.3002 |  |  | 14.3815 | 343.4955 |  |  | EPPGas_00_CCGT-ADC | Existing Power Plant - Aghada CCGT | PJ | GW | DAYNITE
EPPGas_00_CCGT-WG | Existing Power Plant - Whitegate CCGT | ELCGAS | ELCC | 54.42% | 64.72% | 90% | 2010 | 30 | 0.439 | 31.536 | [6 empty] | 8.9596 | 213.9972 |  |  | 16.4644 | 393.2462 |  |  | EPPGas_00_CCGT-WG | Existing Power Plant - Whitegate CCGT | PJ | GW | DAYNITE
EPPDis_00_OCGT-ED | Existing Power Plant - Cushaling OCGT | ELCDIS | ELCC | 31.57% | 0% | 95% | 2010 | 30 | 0.116 | 31.536 |  | 100% |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | EPPDis_00_OCGT-ED | Existing Power Plant - Cushaling OCGT | PJ | GW | DAYNITE
EPPDis_00_OCGT-TP3 | Existing Power Plant - Tawnaghmore 3 OCGT | ELCDIS | ELCC | 31.01% | 0% | 95% | 2003 | 30 | 0.052 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPDis_00_OCGT-TP3 | Existing Power Plant - Tawnaghmore 3 OCGT | PJ | GW | DAYNITE
EPPMsw_00_ST-Meath | Existing Power Plant - Meath Waste-to-Energy ST | ELCMSW | ELCC | 35.29% | 80.53% | 90% | 2011 | 25 | 0.015 | 31.536 | [6 empty] | 0.38092 | 9.0981 |  |  | 1.0793 | 25.7778 |  |  | EPPMsw_00_ST-Meath | Existing Power Plant - Meath Waste-to-Energy ST | PJ | GW | DAYNITE
EPPGas_00_CCGT-GI | Existing Power Plant - Great Island CCGT | ELCGAS | ELCC | 57.69% | 0% | 90% | 2015 | 30 | 0 | 31.536 | [6 empty] | 0 | 0 |  |  | 0 | 0 |  |  | EPPGas_00_CCGT-GI | Existing Power Plant - Great Island CCGT | PJ | GW | DAYNITE
EPPWin_00-ROI | Existing Power Plant - Wind ROI | ELCWIN | ELCC | 100% | 28.5% | 30% |  | 25 | 1.642 | 31.536 | [6 empty] | 14.7579 | 352.4864 |  |  | 14.7579 | 352.4864 |  |  | EPPWin_00-ROI | Existing Power Plant - Wind ROI | PJ | GW | DAYNITE
ECHPBio_00-ROI | Existing CHP - Biomass ROI | ELCBIO | ELCC | 35.29% | 60% | 60% |  | 35 | 0.045 | 31.536 |  |  | 1.8182 | 1 |  |  | 0.85147 | 20.3371 |  |  | 2.4125 | 57.6217 |  | CHP | ECHPBio_00-ROI | Existing CHP - Biomass ROI | PJ | GW | DAYNITE | ELCC
[16 empty] | Tot PP | 85.0866 | 2032.2581 | 1758.5512 |  | 162.9395 | 3891.7428 | 3873.459 | PRE | GRID | Electricity Transmission Grid | PJ | GW | DAYNITE
[16 empty] | Tot CHP | 4.157 | 99.2891 | 182.866 |  | 8.2437 | 196.8976 | 300.4654 | ELE,STS | ESTHyd_00-TH | Existing Electricity Storage (DayNite/Seasonal) - Turlough Hill Pumped Hydro | PJ | GW | DAYNITE | NRGO
[5 empty] | to improve calibration | 0.9 | on AF and EFF | [8 empty] | Tot PS | 1.015 | 24.2431 | 18.2124 |  | 1.3533 | 32.3241 | 29.801
~FI_T: NCAP_Pasti
TechName | Comm-IN | Comm-OUT | 1929 | 1938 | 1950 | 1954 | 1957 | 1967 | 1969 | 1980 | 1987 | 2000 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2010 | 2011 | 2012 | NCAP_BND~FX~2015 | NCAP_BND~0
*Technology Name | Input Commodity | Output Commodity | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW
ECHPGas_00_OCGT-SK | ELCGAS | ELCC,ELCH | [13 empty] | 0.162 | [6 empty] | 2
EPPPea_00_ST-ED | ELCPEA, ELCBIO | ELCC | [9 empty] | 0.118 | [10 empty] | 2
EPPHyd_00-AA | ELCHYD | ELCC | 0.086 | [19 empty] | 2
EPPGas_00_ST-AD | ELCGAS | ELCC | [7 empty] | 0.258 | [12 empty] | 2
EPPGas_00_OCGT-AT | ELCGAS | ELCC | [7 empty] | 0.27 | [12 empty] | 2
EPPHyd_00-ER | ELCHYD | ELCC |  |  | 0.065 | [17 empty] | 2
EPPOil_00_ST-GI | ELCHFO | ELCC | [5 empty] | 0.212 | [14 empty] | 2
EPPHyd_00-LE | ELCHYD | ELCC |  |  |  |  | 0.027 | [15 empty] | 2
EPPHyd_00-LI | ELCHYD | ELCC |  | 0.038 | [18 empty] | 2
EPPPea_00_ST-LR | ELCPEA | ELCC | [12 empty] | 0.091 | [7 empty] | 2
EPPCoa_00_ST-MP | ELCCOA | ELCC | [8 empty] | 0.847 | [11 empty] | 2
EPPGas_00_OCGT-MRC | ELCGAS | ELCC |  |  |  | 0.085 | [16 empty] | 2
EPPGas_00_OCGT-NW | ELCGAS | ELCC | [18 empty] | 0.104 |  | 2
EPPGas_00_OCGT-PBC | ELCGAS | ELCC | [9 empty] | 0.463 | [10 empty] | 2
EPPDis_00_OCGT-RH | ELCDIS | ELCC | [12 empty] | 0.104 | [7 empty] | 2
EPPOil_00_ST-TB | ELCHFO | ELCC | [6 empty] | 0.594 | [13 empty] | 2
EPPDis_00_OCGT-TP1 | ELCDIS | ELCC | [11 empty] | 0.052 | [8 empty] | 2
EPPPea_00_ST-WO | ELCPEA | ELCC | [13 empty] | 0.137 | [6 empty] | 2
EPPGas_00_CCGT-DB | ELCGAS | ELCC | [10 empty] | 0.403 | [9 empty] | 2
EPPGas_00_CCGT-TY | ELCGAS | ELCC | [14 empty] | 0.384 | [5 empty] | 2
EPPGas_00_CCGT-HN | ELCGAS | ELCC | [15 empty] | 0.399 |  |  |  |  | 2
EPPGas_00_CCGT-HNC | ELCGAS | ELCC | [10 empty] | 0.341 | [9 empty] | 2
EPPGas_00_CCGT-ADC | ELCGAS | ELCC | [16 empty] | 0.432 |  |  |  | 2
EPPGas_00_CCGT-WG | ELCGAS | ELCC | [16 empty] | 0.439 |  |  |  | 2
EPPDis_00_OCGT-ED | ELCDIS | ELCC | [16 empty] | 0.116 |  |  |  | 2
EPPDis_00_OCGT-TP3 | ELCDIS | ELCC | [11 empty] | 0.052 | [8 empty] | 2
EPPMsw_00_ST-Meath | ELCMSW | ELCC | [17 empty] | 0.015 |  |  | 2
EPPGas_00_CCGT-GI | ELCGAS | ELCC | [19 empty] | 0.431 | 2
~FI_T: NCAP_Pasti
TechName | Comm-IN | Comm-OUT | 1992 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | NCAP_BND~FX~2013 | NCAP_BND~FX~2014 | NCAP_BND~FX~2015 | NCAP_BND~0
*Technology Name | Input Commodity | Output Commodity | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW | GW
EPPWin_00-ROI | ELCWIN | ELCC | 0.00645 | 0.05078 | 0.005 | 0.00858 | 0.04437 | 0.0034 | 0.0119 | 0.06511 | 0.15105 | 0.16094 | 0.13905 | 0.09885 | 0.21883 | 0.31937 | 0.11432 | 0.22869 | 0.01531 | 0.36486 | 0.26039 | 0.1766 | 2
Base Year Electricity Storage Plants
~FI_T
TechName | *TechDesc | Comm-IN | Comm-OUT | S_EFF | AF | AF~2013 | Life | Stock | Cap2Act | FLO_COST | FLO_DELIV
*Technology Name | Technology Description | Input Commodity | Output Commodity | % | Availability factor | Availability factor | Years | GW |  | Charging Cost | Discharging Cost
ESTHyd_00-TH | Existing Electricity Storage (DayNite/Seasonal) - Turlough Hill Pumped Hydro | ELCC | ELCC | 75% | 11.02% | 16.02% | 150 | 0.292 | 31.536
|  |  | from calib | 61.11% | 8%
Transmission network
~FI_T
TechName | *TechDesc | Comm-IN | Comm-OUT | EFF | ACT_COST | Cap2Act
*Technology Name | Technology Description | Input Commodity | Output Commodity | % | €/GJ
GRID | Electricity Transmission Grid | ELCC | ELCD | 93% |  | 31.536
Note on N5: Power to Heat ratio=0.55 should based on CER "Certification Process for High Efficiency CHP" Decision Paper"
Note on N34: Power to Heat ratio=0.55 should based on CER "Certification Process for High Efficiency CHP" Decision Paper"
Note on E82: Calibrated against Energy Balance

## ELC_FuelTech
Fuel Techs - Sectoral infrastructure
|  | ~FI_T | [6 empty] | ~FI_Process
TechName | Comm-IN | Comm-OUT | EFF | Life | Share-I | Pasti~2012 | INVCOST | NCAP_BND~UP~0 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG
* | [5 empty] | PJa | €/GJa | Interpolation | *
ELCGAS_INF | GASNAT | ELCGAS | 1 | 100 |  | 231.5822 |  |  | PRE | ELCGAS_INF | Fuel tech - Gas (ELC) | PJ | PJa | SEASON
ELCHFO_INF | OILHFO | ELCHFO | 1 | 100 |  | 79.2275 |  |  |  | ELCHFO_INF | Fuel tech - Oil (ELC) | PJ | PJa
ELCHYD_INF | RENHYD | ELCHYD | 1 | 100 |  | 2.5227 |  |  |  | ELCHYD_INF | Fuel tech - Hydro (ELC) | PJ | PJa
ELCPEA_INF | PEAT | ELCPEA | 1 | 100 |  | 25.1748 |  |  |  | ELCPEA_INF | Fuel tech - Peat (ELC) | PJ | PJa
ELCCOA_INF | COABIT | ELCCOA | 1 | 100 |  | 63.9728 |  | 2 |  | ELCBIO_INF | Fuel tech - Biomass (ELC) | PJ | PJa
ELCDIS_INF | OILHFO | ELCDIS | 1 | 100 | 84.42% | 31.2768 |  |  |  | ELCCOA_INF | Fuel tech - Coal (ELC) | PJ | PJa
| OILDST |  |  |  | 15.58% |  |  |  |  | ELCDIS_INF | Fuel tech - Distillate (ELC) | PJ | PJa
ELCMSW_INF | MSWAS | ELCMSW | 1 | 100 |  | 1.2063 |  |  |  | ELCMSW_INF | Fuel tech - Waste (ELC) | PJ | PJa
ELCWIN_INF | RENWIN | ELCWIN | 1 | 100 |  | 15.5346 |  |  |  | ELCWIN_INF | Fuel tech - Wind (ELC) | PJ | PJa
ELCSOL_INF | RENSOL | ELCSOL | 1 | 100 | [5 empty] | ELCSOL_INF | Fuel tech - Solar (ELC) | PJ | PJa
ELCBIO_INF | BIOWOO | ELCBIO | 1 | 100 |  | 11.4442 |  |  |  | ELCBGS_INF | Fuel tech - Biogas (ELC) | PJ | PJa
| BIOWCH | [8 empty] | ELCH2G_INF | Fuel tech - Hydrogen gaseous (ELC) | PJ | PJa | SEASON
ELCBGS_INF | BIOGAS1G | ELCBGS | 1 | 100 | [5 empty] | ELCH2L_INF | Fuel tech - Hydrogen liquid (ELC) | PJ | PJa | SEASON
BIOGAS2G
ELCH2G_INF | SUPH2GC | ELCH2G | 1 | 100
ELCH2L_INF | SUPH2GC | ELCH2L | 1 | 100
Maximum fuel to be supplied (by plant)
(by plant) |  |  |  |  | (by fuel)
Plant | Fuel | Max. cons | Unit |  | Fuel | 2012 | Unit
ECHPGas_00_OCGT-SK | ELCGAS | 8.3814 | PJ |  | ELCBIO | 11.4442 | PJ
EPPPea_00_ST-ED | ELCPEA, ELCBIO | 9.0317 | PJ |  | ELCCOA | 63.9728 | PJ
EPPHyd_00-AA | ELCHYD | 1.2082 | PJ |  | ELCDIS | 31.2768 | PJ
EPPGas_00_ST-AD | ELCGAS | 19.8174 | PJ |  | ELCGAS | 231.5822 | PJ
EPPGas_00_OCGT-AT | ELCGAS | 28.7992 | PJ |  | ELCHFO | 79.2275 | PJ
EPPHyd_00-ER | ELCHYD | 0.90744 | PJ |  | ELCHYD | 2.5227 | PJ
EPPOil_00_ST-GI | ELCHFO | 23.9157 | PJ |  | ELCMSW | 1.2063 | PJ
EPPHyd_00-LE | ELCHYD | 0.28099 | PJ |  | ELCPEA | 25.1748 | PJ
EPPHyd_00-LI | ELCHYD | 0.12611 | PJ |  | ELCWIN | 15.5346 | PJ
EPPPea_00_ST-LR | ELCPEA | 6.9406 | PJ
EPPCoa_00_ST-MP | ELCCOA | 63.9728 | PJ
EPPGas_00_OCGT-MRC | ELCGAS | 9.0868 | PJ
EPPGas_00_OCGT-NW | ELCGAS | 11.6619 | PJ
EPPGas_00_OCGT-PBC | ELCGAS | 28.2482 | PJ
EPPDis_00_OCGT-RH | ELCDIS | 10.1955 | PJ
EPPOil_00_ST-TB | ELCHFO | 55.3118 | PJ
EPPDis_00_OCGT-TP1 | ELCDIS | 5.0491 | PJ
EPPPea_00_ST-WO | ELCPEA | 9.2025 | PJ
EPPGas_00_CCGT-DB | ELCGAS | 21.7092 | PJ
EPPGas_00_CCGT-TY | ELCGAS | 20.3819 | PJ
EPPGas_00_CCGT-HN | ELCGAS | 21.1719 | PJ
EPPGas_00_CCGT-HNC | ELCGAS | 18.189 | PJ
EPPGas_00_CCGT-ADC | ELCGAS | 21.2388 | PJ
EPPGas_00_CCGT-WG | ELCGAS | 22.8966 | PJ
EPPDis_00_OCGT-ED | ELCDIS | 11.0081 | PJ
EPPDis_00_OCGT-TP3 | ELCDIS | 5.0242 | PJ
EPPMsw_00_ST-Meath | ELCMSW | 1.2063 | PJ
EPPGas_00_CCGT-GI | ELCGAS | 0 | PJ
EPPWin_00-ROI | ELCWIN | 15.5346 | PJ
ECHPBio_00-ROI | ELCBIO | 2.4125 | PJ
Note on J10: Alessandro Chiodi: This interpolation rule "2" extrapolates to the time horizon the NCAP_BND = 0 for any period for which a value is not defined. This approach will avoid new future investments in the infrastructure.
Note on G11: Based on split in 2012 from Energy balance

## Commodities
~FI_Comm
Csets | CommName | CommDesc | Unit | CTSLvl | PeakTS | Ctype
*
NRG | ELCGAS | Natural Gas (ELC) | PJ | SEASON
| ELCHFO | Oil (ELC) | PJ
| ELCHYD | Hydro (ELC) | PJ
| ELCPEA | Peat (ELC) | PJ
| ELCBIO | Biomass (ELC) | PJ
| ELCCOA | Coal (ELC) | PJ
| ELCDIS | Distillate (ELC) | PJ
| ELCMSW | Municipal Solid Waste (ELC) | PJ
| ELCWIN | Wind (ELC) | PJ
| ELCSOL | Solar (ELC) | PJ
| ELCBGS | Biogas (ELC) | PJ
| ELCH2G | Hydrogen gasous (ELC) | PJ | SEASON
| ELCH2L | Hydrogen liquid (ELC) | PJ | SEASON
| ELCC | Electricity - Centralized production | PJ | DAYNITE |  | ELC
| ELCD | Electricity - Decentralized production | PJ | DAYNITE |  | ELC
| ELCH | Heat (ELC) | PJ | SEASON
ENV | ELCCO2N | Carbon Dioxide - Combustion (ELC) | kt
| ELCCH4N | Methane (ELC) | kt
| ELCSO2N | Sulphur Oxides (ELC) | kt
| ELCNOXN | Nitrogen Oxide (ELC) | kt
| ELCPM10 | Particulate Matter <10 µm (ELC) | kt
| ELCPM25 | Particulate Matter <2.5 µm (ELC) | kt
| ELCGGAS | Blended Gas wt Biogas (ELC) | PJ
| ELCHGAS | Blended Gas wt Hydrogen (ELC) | PJ

## Emi
Emission - Dynamic coefficients
~COMEMI
| CommName | ELCGAS | ELCGGAS | ELCHGAS | ELCHFO | ELCHYD | ELCPEA | ELCCOA | ELCDIS | ELCMSW | ELCWIN | ELCSOL | *Unit
| ELCCO2N | 56.1 |  |  | 77.4 | 0 | 108 | 99 | 74.1 | 45 | 0 | 0 | kt/PJ
ELCCH4N
ELCSO2N
ELCNOXN
ELCPM10
ELCPM25

## EB2012
2012 Units = ktoe | NACE (Rev 2) | Coal | Bituminous Coal | Anthracite + Manufactured Ovoids | Coke | Lignite \ Brown Coal Briquettes | Peat | Milled Peat | Sod Peat | Briquettes | Oil | Crude | Refinery Gas | Gasoline | Kerosene | Jet Kerosene | Fueloil | LPG | Gasoil / Diesel /DERV | Petroleum Coke | Naphta | Bitumen | White Spirit | Lubricants | Natural Gas | Renewables | Hydro | Wind | Biomass & Renewable Waste | Landfill Gas | Biogas | Liquid Biofuel | Solar | Geothermal | Non-Renewable Waste | Electricity | Heat | TOTAL
Indigenous Production |  | 0 | 0 |  |  |  | 315.3564 | 187.6524 | 127.704 |  | 0 | [13 empty] | 171.4975 | 757.306 | 69.002 | 344.9011 | 222.8651 | 42.9794 | 12.9235 | 23.9721 | 10.2583 | 30.4045 | 43.833 |  |  | 1287.9929
Imports |  | 1346.8347 | 1293.3248 | 41.4546 |  | 12.0553 | 0 |  |  |  | 8265.9176 | 3005.4214 | 0 | 1079.751 | 532.715 | 763.4367 | 196.4393 | 104.5556 | 2182.8744 | 125.355 | 0 | 238.1956 | 0.97743 | 36.1964 | 3846.4507 | 79.6219 |  |  | 15.3922 |  |  | 64.2297 |  |  |  | 67.39 |  | 13606.2148
Exports |  | 9.311 | 0 | 8.9073 |  | 0.40368 | 8.8697 |  |  | 8.8697 | 1772.3669 | 0 |  | 433.6203 | 5.988 | 0.47673 | 962.4542 | 37.7243 | 316.419 | 0.2221 | 9.0163 | 0.017207 | 0.005255 | 6.4236 | 0 | 0.0028858 |  |  | 0.0028858 |  |  | 0 |  |  |  | 31.8312 |  | 1822.3817
Mar. Bunkers |  | 0 |  |  |  |  | 0 |  |  |  | 128.5388 | [5 empty] | 23.6965 |  | 104.8423 | [6 empty] | 0 | [11 empty] | 128.5388
Stock Change |  | 155.2644 | 148.5535 | 5.5183 |  | 1.1926 | 464.6293 | 457.3668 | 0 | 7.2625 | 149.9716 | 131.9154 |  | 11.885 | -32.9937 | 2.1154 | 33.9079 | -0.41188 | 20.3364 | -11.3617 | -5.4212 | 0 | 0 | 0 | 15.0163 | -2.1172 |  |  | 1.2742 |  |  | -3.3914 | [5 empty] | 782.7644
Primary Energy Supply (incl non-energy) |  | 1492.788 | 1441.8783 | 38.0655 | 0 | 12.8442 | 771.1159 | 645.0191 | 127.704 | -1.6072 | 6514.9835 | 3137.3368 | 0 | 658.0156 | 493.7333 | 765.0753 | -755.8034 | 66.4194 | 1781.9496 | 113.7712 | -14.4375 | 238.1784 | 0.97218 | 29.7728 | 4032.9645 | 834.8078 | 69.002 | 344.9011 | 239.5286 | 42.9794 | 12.9235 | 84.8104 | 10.2583 | 30.4045 | 43.833 | 35.5588 | 0 | 13726.0517
Primary Energy Requirement (excl. non-energy) |  | 1492.788 | 1441.8783 | 38.0655 | 0 | 12.8442 | 771.1159 | 645.0191 | 127.704 | -1.6072 | 6246.0602 | 3137.3368 | 0 | 658.0156 | 493.7333 | 765.0753 | -755.8034 | 66.4194 | 1781.9496 | 113.7712 | -14.4375 | 0 | 0 | 0 | 4032.9645 | 834.8078 | 69.002 | 344.9011 | 239.5286 | 42.9794 | 12.9235 | 84.8104 | 10.2583 | 30.4045 | 43.833 | 35.5588 | 0 | 13457.1284
Transformation Input |  | 1160.1105 | 1160.1105 | 0 | 0 | 0 | 656.955 | 656.955 | 0 | 0 | 3193.2216 | 3137.3368 | 8.7414 | 0 | 0 | 0 | 39.3853 | 0.4908 | 7.2673 | 0 | 0 | 0 | 0 | 0 | 2328.2369 | 112.7848 | 0 | 0 | 65.6561 | 42.9794 | 4.1493 | 0 | 0 | 0 | 18.3487 | 49.0166 | 0 | 7518.6741
Public Thermal Power Plants |  | 1160.1105 | 1160.1105 |  |  |  | 549.9992 | 549.9992 | 0 |  | 46.6526 | [5 empty] | 39.3853 |  | 7.2673 | [5 empty] | 1994.4963 | 103.8518 |  |  | 60.8724 | 42.9794 |  |  |  |  | 18.3487 |  |  | 3873.459
Combined Heat and Power Plants |  | 0 | 0 |  |  |  | 7.3138 | 7.3138 |  |  | 9.2322 |  | 8.7414 |  |  |  | 0 | 0.4908 | 0 | [5 empty] | 274.9864 | 8.933 |  |  | 4.7837 |  | 4.1493 | [6 empty] | 300.4654
Pumped Storage Consumption | [35 empty] | 29.801 |  | 29.801
Briquetting Plants |  | 0 |  |  |  |  | 99.642 | 99.642 |  |  | 0 | [14 empty] | 0 | [11 empty] | 99.642
Oil Refineries & other energy sector |  | 0 |  |  |  |  | 0 |  |  |  | 3137.3368 | 3137.3368 | [12 empty] | 58.7542 | 0 | [9 empty] | 19.2156 |  | 3215.3066
Transformation Output |  | 0 | 0 | 0 | 0 | 0 | 87.0663 | 0 | 0 | 87.0663 | 3100.4499 | 0 | 39.3656 | 587.0093 | 139.3376 | 0 | 946.9378 | 81.8135 | 1295.8924 | 0 | 10.0936 | 0 | 0 | 0 | 0 | 37.7753 | 0 | 0 | 20.6529 | 15.0158 | 2.1066 | 0 | 0 | 0 | 3.9249 | 1959.6297 | 0 | 5188.8461 | EFF
Public Thermal Power Plants |  | 0 |  |  |  |  | 0 |  |  |  | 0 | [14 empty] | 33.7642 |  |  | 18.7484 | 15.0158 |  |  |  |  | 3.9249 | 1758.5512 |  | 1758.5512 | 45.4%
Combined Heat and Power Plants - Electricity |  | 0 |  |  |  |  | 0 |  |  |  | 0 | [14 empty] | 4.0111 |  |  | 1.9045 |  | 2.1066 |  |  |  |  | 182.866 |  | 182.866 | 60.86%
Combined Heat and Power Plants - Heat | [25 empty] | 0 | [11 empty] | 0
Pumped Storage Generation | [35 empty] | 18.2124 |  | 18.2124
Briquetting Plants | [6 empty] | 87.0663 |  |  | 87.0663 | 0 | [14 empty] | 0 | [11 empty] | 87.0663
Oil Refineries | [6 empty] | 0 |  |  |  | 3100.4499 |  | 39.3656 | 587.0093 | 139.3376 | 0 | 946.9378 | 81.8135 | 1295.8924 |  | 10.0936 |  |  |  |  | 0 | [11 empty] | 3100.4499
Exchanges and transfers |  | 17.1975 | -11.2924 | 28.4898 | 0 | 0 | 0 | 0 | 0 | 0 | -18.1945 | 0 | 0 | 0.024707 | 169.0957 | -168.7128 | 0.56981 | 0 | -1.9745 | -17.1975 | 0 | 0 | 0 | 0 | 0 | -413.9587 | -69.002 | -344.9011 | 0 | 0 | 0 | 0 | -0.05554 | 0 | 0 | 413.9587 | 0 | -0.99703
Electricity | [25 empty] | -413.9587 | -69.002 | -344.9011 |  |  |  |  | -0.05554 |  |  | 413.9587 |  | 0
Heat | [37 empty] | 0
Other |  | 17.1975 | -11.2924 | 28.4898 | [6 empty] | -18.1945 |  |  | 0.024707 | 169.0957 | -168.7128 | 0.56981 |  | -1.9745 | -17.1975 | [5 empty] | 0 | [11 empty] | -0.99703
Own Use and Distribution Losses |  | 0 |  |  |  |  | 14.4674 | 14.4674 |  |  | 41.0915 |  | 30.6242 |  |  |  | 0 | 10.3187 | 0.14853 | [5 empty] | 61.0264 | 0 | [9 empty] | 270.3502 |  | 386.9355
Available Final Energy Consumption |  | 349.875 | 270.4755 | 66.5554 | 0 | 12.8442 | 186.7599 | -26.4033 | 127.704 | 85.4591 | 6362.9259 | -4.5475e-13 | 0 | 1245.0496 | 802.1666 | 596.3625 | 152.3189 | 137.4234 | 3068.4517 | 96.5737 | -4.3439 | 238.1784 | 0.97218 | 29.7728 | 1643.7011 | 308.0644 | 0 | 0 | 173.8725 | 0 | 8.7742 | 84.8104 | 10.2027 | 30.4045 | 25.4843 | 2089.7804 | 0 | 10966.5909
Non-Energy Consumption |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.9233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 238.1784 | 0.97218 | 29.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268.9233
Final non-Energy Consumption (Feedstocks) |  | 0 |  |  |  |  | 0 |  |  |  | 268.9233 | [10 empty] | 238.1784 | 0.97218 | 29.7728 | 0 | 0 | [11 empty] | 268.9233
Total Final Energy Consumption |  | 328.4576 | 251.3623 | 65.1803 | 0 | 11.9149 | 215.2746 | 0.74258 | 127.704 | 86.828 | 6093.1983 | 0 | 0 | 1272.4461 | 758.3802 | 585.674 | 118.381 | 137.0065 | 3120.6554 | 100.6544 | 0 | 0 | 0 | 0 | 1627.2131 | 311.0552 | 0 | 0 | 176.8068 | 0 | 8.7742 | 84.867 | 10.2027 | 30.4045 | 25.4843 | 2078.1077 | 0 | 10678.7907
Industry* |  | 86.4782 | 86.4782 | 0 |  |  | 0.74258 | 0.74258 | 0 | 0 | 514.1548 | 0 | 0 | 0 | 75.838 | 0 | 108.532 | 95.8108 | 143.2192 | 90.7548 | 0 | 0 | 0 | 0 | 625.6776 | 134.9592 | 0 | 0 | 130.0967 |  | 4.8626 | 0 | 0 | 0 | 25.4843 | 787.9217 | 0 | 2175.4183
Non-Energy Mining | 05-09 | 0 | 0 |  |  |  | 0 |  |  |  | 37.3747 |  |  |  | 2.3932 |  | 0.70877 | 0.16302 | 34.1097 | 0 |  |  |  |  | 10.2206 | 0 | [9 empty] | 56.4118 |  | 104.0071
Food & beverages | 10-11 | 15.63 | 15.63 |  |  |  | 0.74258 | 0.74258 |  |  | 117.5046 |  |  |  | 44.553 |  | 13.1947 | 27.3197 | 32.4372 | 0 |  |  |  |  | 89.8637 | 18.2465 |  |  | 13.384 |  | 4.8626 |  |  |  |  | 167.6993 |  | 409.6867
Textiles and textile products | 13-14 | 0 | 0 |  |  |  | 0 |  |  |  | 2.3091 |  |  |  | 0.98604 |  | 0.29203 | 0.042071 | 0.98899 | 0 |  |  |  |  | 0.97931 | 0 | [9 empty] | 10.0362 |  | 13.3246
Wood and wood products | 16 | 0.053396 | 0.053396 |  |  |  | 0 |  |  |  | 2.7767 |  |  |  | 0.34794 |  | 0.10305 | 0.22087 | 2.1048 | 0 |  |  |  |  | 1.7472 | 95.2615 |  |  | 95.2615 | [6 empty] | 33.7341 |  | 133.5729
Pulp, paper, publishing and printing | 17-18 | 0.23361 | 0.23361 |  |  |  | 0 |  |  |  | 2.7933 |  |  |  | 0.8063 |  | 0.23879 | 0.21035 | 1.5378 | 0 |  |  |  |  | 2.8898 | 0 | [9 empty] | 18.4113 |  | 24.328
Chemicals & man-made fibres | 20-21 | 0 | 0 |  |  |  | 0 |  |  |  | 25.3173 |  |  |  | 10.5987 |  | 3.1389 | 2.4769 | 9.1028 | 0 |  |  |  |  | 55.4867 | 0 |  |  | 0 | [6 empty] | 142.8913 |  | 223.6953
Rubber and plastic products | 22 | 0 | 0 |  |  |  | 0 |  |  |  | 9.0263 |  |  |  | 0.068047 |  | 0.020153 | 4.9433 | 3.9948 | 0 |  |  |  |  | 3.838 | 0 | [9 empty] | 34.5489 |  | 47.4131
Other non-metallic mineral products | 23 | 69.1561 | 69.1561 |  |  |  | 0 |  |  |  | 146.3015 |  |  |  | 7.1758 |  | 2.1252 | 1.1149 | 45.1309 | 90.7548 |  |  |  |  | 14.4659 | 21.4513 |  |  | 21.4513 | [5 empty] | 25.4843 | 50.0292 |  | 326.8882
Basic metals and fabricated metal products | 24-25 | 0 | 0 |  |  |  | 0 |  |  |  | 93.5051 |  |  |  | 0 |  | 86.072 | 4.5594 | 2.8738 | 0 |  |  |  |  | 328.8429 | 0 | [9 empty] | 64.0148 |  | 486.3628
Machinery and equipment n.e.c. | 28 | 0 | 0 |  |  |  | 0 |  |  |  | 5.4002 |  |  |  | 0.37105 |  | 0.10989 | 1.8669 | 3.0524 | 0 |  |  |  |  | 4.6898 | 0 | [9 empty] | 20.0432 |  | 30.1332
Electrical and optical equipment | 26-27 | 0.0066745 | 0.0066745 |  |  |  | 0 |  |  |  | 35.1575 |  |  |  | 0.30685 |  | 0.090878 | 33.0045 | 1.7553 | 0 |  |  |  |  | 105.5296 | 0 | [9 empty] | 97.1075 |  | 237.8013
Transport equipment manufacture | 29-30 | 0 | 0 |  |  |  | 0 |  |  |  | 4.0929 |  |  |  | 0.24009 |  | 0.071105 | 2.9765 | 0.80517 | 0 |  |  |  |  | 1.5949 | 0 | [9 empty] | 16.6114 |  | 22.2992
Other manufacturing | 31-33, 12 & 15 | 1.3983 | 1.3983 |  |  |  | 0 |  |  | 0 | 32.5956 |  |  |  | 7.9911 |  | 2.3666 | 16.9124 | 5.3255 | 0 |  |  |  |  | 5.5292 | 0 | [9 empty] | 76.3826 |  | 115.9058
Transport |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4083.5547 | 0 | 0 | 1272.4461 | 0 | 585.674 | 0 | 0.99991 | 2224.4347 | 0 | 0 | 0 | 0 | 0 | 0 | 84.867 | 0 | 0 | 0 | 0 | 0 | 84.867 | 0 | 0 | 0 | 3.8691 | 0 | 4172.2908
Road Freight |  | 0 |  |  |  |  | 0 |  |  |  | 613.0956 | [7 empty] | 613.0956 | [6 empty] | 16.1983 | [5 empty] | 16.1983 | [5 empty] | 629.294
Road Light Goods Vehicle | [10 empty] | 315.774 | [7 empty] | 315.774 | [6 empty] | 8.3429 | [5 empty] | 8.3429 | [5 empty] | 324.1169
Road Private Car |  | 0 |  |  |  |  | 0 |  |  |  | 2038.7666 |  |  | 1176.3582 |  |  |  | 0.99991 | 861.4085 | [6 empty] | 49.2915 | [5 empty] | 49.2915 | [5 empty] | 2088.0581
Public Passenger Services |  | 0 |  |  |  |  | 0 |  |  |  | 149.6753 |  |  | 24.0513 |  |  |  |  | 125.624 | [6 empty] | 3.8598 | [5 empty] | 3.8598 | [5 empty] | 153.5352
Rail |  | 0 |  |  |  |  | 0 |  |  |  | 38.4624 | [7 empty] | 38.4624 | [6 empty] | 0 | [5 empty] | 0 |  |  |  | 3.8691 |  | 42.3315
Domestic Aviation |  | 0 |  |  |  |  | 0 |  |  |  | 3.8016 |  |  | 0.73269 |  | 3.069 | [9 empty] | 0 | [11 empty] | 3.8016
International Aviation |  | 0 |  |  |  |  | 0 |  |  |  | 582.6051 |  |  |  |  | 582.6051 | [9 empty] | 0 | [11 empty] | 582.6051
Fuel Tourism |  | 0 |  |  |  |  | 0 |  |  |  | 249.1219 |  |  | 41.9285 |  |  |  |  | 207.1934 | [6 empty] | 6.4169 | [5 empty] | 6.4169 | [5 empty] | 255.5387
Navigation |  | 0 |  |  |  |  | 0 |  |  |  | 59.2019 | [7 empty] | 59.2019 | [6 empty] | 0 | [11 empty] | 59.2019
Unspecified |  | 0 |  |  |  |  | 0 |  |  |  | 33.0502 |  |  | 29.3754 |  |  | 0 |  | 3.6748 | [6 empty] | 0.75755 | [5 empty] | 0.75755 | [5 empty] | 33.8078
Residential |  | 241.9795 | 164.8842 | 65.1803 |  | 11.9149 | 214.532 |  | 127.704 | 86.828 | 910.1755 |  |  | 0 | 682.5422 |  | 0 | 33.0567 | 184.6773 | 9.8993 |  |  |  |  | 600.494 | 60.629 |  |  | 27.5967 |  |  |  | 10.0366 | 22.9957 |  | 698.3602 |  | 2726.1701
Commercial/Public Services |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360.2091 | 0 | 0 | 0 | 0 | 0 | 9.849 | 7.1391 | 343.2199 | 0.00036475 | 0 | 0 | 0 | 0 | 401.0415 | 30.6 | 0 | 0 | 19.1134 | 0 | 3.9117 | 0 | 0.16614 | 7.4088 | 0 | 539.9687 | 0 | 1331.8192
Commercial Services |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 233.016 |  |  |  | 0 |  | 0.96093 | 5.3143 | 226.7404 | 0.00036475 |  |  |  |  | 175.7654 | 26.6883 |  |  | 19.1134 |  |  |  | 0.16614 | 7.4088 |  | 387.1236 |  | 822.5933
Public Services |  | 0 |  |  |  |  | 0 |  | 0 | 0 | 127.1931 | [5 empty] | 8.8887 | 1.8248 | 116.4795 | [5 empty] | 225.3224 | 3.9117 |  |  |  |  | 3.9117 |  |  |  |  | 152.8675 |  | 509.2947
Agricultural |  | 0 | 0 |  |  |  | 0 |  |  |  | 202.5797 |  |  | 0 | 0 |  |  | 0 | 202.5797 | [5 empty] | 0 | 0 | [9 empty] | 47.988 |  | 250.5677
Fisheries |  | 0 |  |  |  |  | 0 |  |  |  | 22.5245 | [7 empty] | 22.5245 | [6 empty] | 0 | [11 empty] | 22.5245
Statistical Difference |  | 21.4174 | 19.1131 | 1.375 | 0 | 0.92924 | -28.5147 | -27.1458 | 0 | -1.3689 | 0.8043 | -4.5475e-13 | 0 | -27.3965 | 43.7864 | 10.6885 | 33.9379 | 0.41693 | -52.2037 | -4.0807 | -4.3439 | 0 | 0 | 0 | 16.488 | -2.9908 | 0 | 0 | -2.9343 | 0 | 0 | -0.056547 | 0 | 0 | 0 | 11.6727 | 0 | 18.8769
* Industry sub-sectoral breakdown is based on the CIP 2009.
Last Updated : 30th September 2015
2012 provisional data
2012 provisional data based on 2011 breakdown
2011 data
Sod peat is estimated due to new legislation and the methodology is under review
Statistical differences may exist for crude oil between the calculated primary energy requirement and the observed refinery input

## Wind IWEA
Wind Farm | Capacity | Comission Date | Potential Retirement year | Lifetime | Retirement | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Bellacorick | 6.45 | 1992 | 2017 | 25 |  | 6.45 | 64.36 | 275.83 | 937.04 | 983.57 | 176.6 | 0
Kilronan | 5 | 1997 | 2022
Corrie Mt. | 4.8 | 1997 | 2022
Spion Kop | 1.2 | 1997 | 2022 |  |  | 2012 (Oct)
Golagh | 15 | 1997 | 2022 |  | Capacity Statement | 1642 | MW
Cronalaght | 4.98 | 1997 | 2022
Drumlough | 4.8 | 1997 | 2022
Cark | 15 | 1997 | 2022 |  |  | 1992 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | Unit
Crockahenny | 5 | 1998 | 2023 |  | IWEA Installated Cap | 6.45 | 50.78 | 5 | 8.58 | 44.37 | 3.4 | 11.9 | 65.11 | 151.05 | 160.94 | 139.05 | 98.85 | 218.83 | 319.37 | 114.32 | 228.69 | 128.49 | 251.68 | 260.39 | 176.6 | MW
Currabwee | 4.62 | 1999 | 2024 |  | Correction | [16 empty] | 15.31 | 364.86 |  |  | MW
Inverin 1 | 3.3 | 1999 | 2024 |  |  | 2017 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Inverin 2 | 0.66 | 1999 | 2024
Beenageeha | 3.96 | 2000 | 2025
Tursillagh/1 | 15 | 2000 | 2025
Beal Hill/1 | 1.65 | 2000 | 2025
Milane Hill | 5.94 | 2000 | 2025
Largan Hill | 5.94 | 2000 | 2025
Culliagh | 11.88 | 2000 | 2025
Blackbanks/1 | 3.4 | 2001 | 2026
Carnsore | 11.9 | 2002 | 2027
Bel Hill/2 | 2.55 | 2003 | 2028
Raheen Barr/ Castlebar | 18.7 | 2003 | 2028
Kingsmountain | 23.75 | 2003 | 2028
Meenadreen | 3.4 | 2003 | 2028
Burtonport | 0.66 | 2003 | 2028
Meenanilta/Ballybofey/1 | 2.55 | 2003 | 2028
Snugborough | 13.5 | 2003 | 2028
Tursillagh/2 | 6.8 | 2004 | 2029
Mienvee I | 0.66 | 2004 | 2029
Curraghgraigue | 2.55 | 2004 | 2029
Mienvee II | 0.19 | 2004 | 2029
Moanmore | 12.6 | 2004 | 2029
Sonnagh Old | 7.65 | 2004 | 2029
Cuillalea/Liltmagh | 4.99 | 2004 | 2029
Anarget | 1.98 | 2004 | 2029
Meenanilta/Ballybofey/2 | 2.45 | 2004 | 2029
Anagret Ext | 0.02 | 2004 | 2029
Meentycat | 70.96 | 2004 | 2029
Gartnaneane | 10.5 | 2004 | 2029
Gartnaneane 2 | 4.5 | 2004 | 2029
Arklow/Offshore | 25.2 | 2004 | 2029
Mount Eagle Windfarm Ltd | 5.1 | 2005 | 2030
Coomatallin | 5.95 | 2005 | 2030
Kealkill | 8.5 | 2005 | 2030
Booltiagh | 19.45 | 2005 | 2030
Derrybrien | 59.5 | 2005 | 2030
Altagowlan | 7.65 | 2005 | 2030
Blackbanks/2 | 6.8 | 2005 | 2030
Moneenatieve | 3.96 | 2005 | 2030
Ballywater | 31.5 | 2005 | 2030
Kilbranish | 4.99 | 2005 | 2030
Cronelea Upper | 2.55 | 2005 | 2030
Cronelea 1 | 4.99 | 2005 | 2030
Gneeves | 9.35 | 2006 | 2031
Kilvinane | 4.5 | 2006 | 2031
Lahanaght Hill | 4.25 | 2006 | 2031
Taurbeg | 26 | 2006 | 2031
Carrig | 2.55 | 2006 | 2031
Skehanagh | 4.25 | 2006 | 2031
Ballinlough/Ikerrin | 2.55 | 2006 | 2031
Ballinveny | 2.55 | 2006 | 2031
Caranne Hill 1 | 3.4 | 2006 | 2031
Geevagh | 4.95 | 2006 | 2031
Sorne Hill | 31.5 | 2006 | 2031
Beam Hill | 14 | 2006 | 2031
Richfield | 20.25 | 2006 | 2031
Richfield 2 | 6.75 | 2006 | 2031
Dundalk IT | 0.5 | 2006 | 2031
Dunmore 1 | 1.7 | 2006 | 2031
Kilgarvan/Coomagearlaghy | 42.5 | 2007 | 2032
Glanlee 1 (Midas) | 29.8 | 2007 | 2032
Tournafulla | 7.5 | 2007 | 2032
Lackan 1 | 6 | 2007 | 2032
Killybegs Wind Farm Ltd | 2.55 | 2007 | 2032
Ballywater 2 | 10.5 | 2007 | 2032
Clahane (Pallas Wind Farm) | 37.8 | 2008 | 2033
Mount Eagle (2) | 1.7 | 2008 | 2033
Muingnaminanne | 15.3 | 2008 | 2033
Ballybane (Glanta Commons) | 19.55 | 2008 | 2033
Coomacheo | 41.23 | 2008 | 2033
Knockawarriga | 22.5 | 2008 | 2033
Tounafulla II | 17.2 | 2008 | 2033
Beallough | 1.7 | 2008 | 2033
Moneenatieve 2 | 0.29 | 2008 | 2033
Loughderryduff | 7.65 | 2008 | 2033
Lurganboy | 4.99 | 2008 | 2033
Meenachullalan | 11.9 | 2008 | 2033
Mullananalt | 7.5 | 2008 | 2033
Mountain Lodge | 24.8 | 2008 | 2033
Mountain Lodge 2 | 3 | 2008 | 2033
Lios na Carraige | 0.02 | 2008 | 2033
Cronelea Upper 2 | 1.7 | 2008 | 2033
Coomagearlahy II (Sillahertane) | 8.5 | 2009 | 2034
Coomagearlahy III (Inchincoosh) | 30 | 2009 | 2034
Coomacheo ll | 18 | 2009 | 2034
Boggeragh | 57 | 2009 | 2034
Lacka cross | 4.5 | 2009 | 2034
Reenascreena Wind Farm | 4.5 | 2009 | 2034
Ballybane/Glanta Commons ll | 8.4 | 2009 | 2034
Knockastanna | 7.5 | 2009 | 2034
Dromada | 28.5 | 2009 | 2034
Slievereagh | 3 | 2009 | 2034
Lisheen 1 | 36 | 2009 | 2034
Derrynadiva | 8.5 | 2009 | 2034
Mace Upper | 2.55 | 2009 | 2034
Sorne Hill 2 | 7.4 | 2009 | 2034
Glackmore 1 | 0.6 | 2009 | 2034
Glackmore 2 | 1.4 | 2009 | 2034
Glackmore 3 | 0.3 | 2009 | 2034
Meentycat 2 | 14 | 2009 | 2034
Flughland | 9.2 | 2009 | 2034
Meenkeeragh | 4.2 | 2009 | 2034
Ratrussan/Bindoo | 48 | 2009 | 2034
Mountain Lodge 3 | 5.82 | 2009 | 2034
Rahora/Tullogher | 4.25 | 2009 | 2034
Cronelea 2 | 4.5 | 2009 | 2034
Dunmore 2 | 2.5 | 2009 | 2034
Donaghmede Fr Collins Park | 0.25 | 2009 | 2034
Ballincollig Hill | 15 | 2010 | 2035
Carrons | 4.99 | 2010 | 2035
Cuillalea 2 | 1.59 | 2010 | 2035
Kingsmountain 2 | 11.05 | 2010 | 2035
Garvagh Tullynahew | 22 | 2010 | 2035
Garvagh Glebe Wind Farm | 26 | 2010 | 2035
Shannagh | 2.55 | 2010 | 2035
Drumlough Hill 2 | 9.99 | 2010 | 2035
Tullow Mushroon Growers Ltd | 0.13 | 2010 | 2035
Gortahile | 21 | 2010 | 2035
Owenstown | 0.02 | 2010 | 2035
Crocane | 1.7 | 2011 | 2036
Carigcannon Wind Farm | 20 | 2011 | 2036
Bawnmore Wind Farm | 24 | 2011 | 2036
Ratcahill | 12.5 | 2011 | 2036
Grouse Lodge | 15 | 2011 | 2036
Dromdeeveen 1 | 10.5 | 2011 | 2036
Dromdeeveen 2 | 16.5 | 2011 | 2036
Glenough Wind Farm | 33 | 2011 | 2036
Curraghgraigue 2 | 2.44 | 2011 | 2036
Burren/Lenanevea | 4.65 | 2011 | 2036
Seltanaveeny | 4.6 | 2011 | 2036
Skrine | 4.6 | 2011 | 2036
Tullnamoyle Wind Farm | 9 | 2011 | 2036
Corkermore | 15 | 2011 | 2036
Anarget | 0.5 | 2011 | 2036
Meenkeeragh II | 0.4 | 2011 | 2036
Meenanilta III | 3.4 | 2011 | 2036
Corneen | 3 | 2011 | 2036
Castledockrell 1 | 20 | 2011 | 2036
Castledockrell 2 | 2 | 2011 | 2036
Castledockrell 3 | 3.3 | 2011 | 2036
Castledockrell 4 | 16.1 | 2011 | 2036
Ballymartin | 6 | 2011 | 2036
Country Crest | 0.5 | 2011 | 2036
Knockaneden | 9 | 2012 | 2037
Clydaghroe | 4.99 | 2012 | 2037
Caher Downey (1) | 10 | 2012 | 2037
Templederry Wind Farm | 3.9 | 2012 | 2037
Garracummer Wind Farm | 36.9 | 2012 | 2037
Carrowleagh Windfarm | 34.15 | 2012 | 2037
Ballycadden 1 | 14.45 | 2012 | 2037
Ballycadden 2 | 11.5 | 2012 | 2037
Ballaman | 3.6 | 2012 | 2037
Knocknagoum | 44.5 | 2013 | 2038
Garranareagh Wind Farm | 8.75 | 2013 | 2038
Pluckanes Wind Farm | 0.85 | 2013 | 2038
Knockacummer 1 | 87 | 2013 | 2038
Athea 1 | 34.35 | 2013 | 2038
Lisheen 1a | 19 | 2013 | 2038
Hollyford Wind Farm | 9 | 2013 | 2038
Booltiagh 2 | 3 | 2013 | 2038
Booltiagh 3 | 9 | 2013 | 2038
Ballynancoran 1 | 4 | 2013 | 2038
Gibbet Hill | 15 | 2013 | 2038
Knocknalour 1 | 5 | 2013 | 2038
Knocknalour 2 | 3.95 | 2013 | 2038
Ballymartin 2 | 8.28 | 2013 | 2038
DePuy | 2.5 | 2014 | 2039
Janssen Wind Energy Project | 2 | 2014 | 2039
Ballycureen Wind Farm | 4.99 | 2014 | 2039
Monaincha Bog Gate 2 | 3.4 | 2014 | 2039
Monaincha Bog Gate 3 | 32.55 | 2014 | 2039
Kill Hill phase 1 | 36.8 | 2014 | 2039
Bruckana | 39.6 | 2014 | 2039
Leitir Guingaid | 40.9 | 2014 | 2039
Carrickheeney | 7.65 | 2014 | 2039
Faughary | 6 | 2014 | 2039
Mount Lucas | 84 | 2014 | 2039
Cloghboola | 46 | 2015 | 2040
Glanta Commons (Ballybane 2A) | 11.5 | 2015 | 2040
Boggeragh 2 Wind Farm | 25 | 2015 | 2040
Boggeragh 2 (Formerly Killavoy (1)) | 18 | 2015 | 2040
Slievereagh 2 | 1.6 | 2015 | 2040
Barranafaddock | 32.4 | 2015 | 2040
Woodhouse | 20 | 2015 | 2040
Carrownaweelaun Wind Farm | 4.6 | 2015 | 2040
Acres | 17.5 | 2015 | 2040
2443.85
ROI
http://www.iwea.com/windfarmsinireland