## SRV_DC_Commodities
Fixed layout table
* Define the commodities used in this workbook
Commodities
~FI_Comm
Csets | Region | CommName | CommDesc | Unit | LimType | CTSLvl | PeakTS | Ctype
*Commodity Set Membership | Region Name | Commodity Name | Commodity Description | Unit | Sense of the Balance EQN. | Timeslice Level | Peak Monitoring | Electricity Indicator
NRG |  | SRVELC-DC-C | Electricity (SRV) - Data Centers - Cooling | PJ |  | DAYNITE |  | ELC
|  | SRVHET-DC-LT | Heat (SRV) - Data Centers - Low Temperature | PJ |  | DAYNITE
NRG |  | SRVHET-LT | Heat (SRV) - Low Temperature | PJ |  | DAYNITE

## SRV_DC_Processes
[5 empty] | ~FI_T | [14 empty] | ~FI_Process
TechName | TechDesc | Comm-IN | Comm-OUT | YEAR | CURR | START | EFF | Share-I~2020 | Share-I~2025 | Share-I~2030 | Share-I~2040 | Share-I~2050 | Share-I~0 | INVCOST | FIXOM | VAROM | AFA | PRC_CAPACT | LIFE | Sets | Region | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
\I:Technology Name | Technology Description | Input Commodity | Output Commodity | Year | Currency | Starting Year | Technical Efficiency | [5 empty] | Interpolation rule for Share | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Annual Availability Factor | Capacity to Activity Factor | Lifetime of Process | *Process Set Membership | Region Name | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
*Units | [6 empty] | - | - | - | - |  | - |  | MEUR/GW | MEUR/GW | MEUR/PJ | - | - | Years | PRE |  | S-DCE-CS-HP_N1 | Commercial Services - Data Centres - Heat Pump for Upgrading Excess Heat | PJ | GW | DAYNITE |  | YES
S-DCE-CS-HP_N1 | Commercial Services - Data Centres - Heat Pump for Upgrading Excess Heat | SRVHET-LT | HETC | 2020 | EUR15 | 2020 | 1 | 0.78261 | 0.78723 | 0.79167 | 0.79592 | 0.8 | 5 | 856.2467 | 2 | 0.60833 | 0.98 | 31.536 | 25 |  |  | S-DCE-CS-HE_N1 | Commercial Services - Data Centres - Heat Exchanger for Excess Heat | PJ | GW | DAYNITE |  | YES
|  | SRVELC | [5 empty] | 0.21739 | 0.21277 | 0.20833 | 0.20408 | 0.2 | 5
|  |  |  | 2025 | EUR15 | [8 empty] | 856.2467 |  |  |  |  | 25
|  |  |  | 2030 | EUR15 | [8 empty] | 761.1082 |  |  |  |  | 25
|  |  |  | 2040 | EUR15 | [8 empty] | 761.1082 |  |  |  |  | 25
|  |  |  | 2050 | EUR15 | [8 empty] | 761.1082 |  |  |  |  | 25
S-DCE-CS-HE_N1 | Commercial Services - Data Centres - Heat Exchanger for Excess Heat | SRVHET-DC-LT | SRVHET-LT | 2020 | EUR20 | 2020 | 1 | [6 empty] | 41.4 | 0.351 |  |  | 31.536 | 25
|  |  |  | 2025 | EUR20 |  | 1 | [6 empty] | 40.3753 | 0.35813 |  |  |  | 25
|  |  |  | 2030 | EUR20 |  | 1 | [6 empty] | 39.376 | 0.36125 |  |  |  | 25
|  |  |  | 2040 | EUR20 |  | 1 | [6 empty] | 37.4509 | 0.34638 |  |  |  | 25
|  |  |  | 2050 | EUR20 |  | 1 | [6 empty] | 35.6199 | 0.3295 |  |  |  | 25

## HP_data
Source: Technology Data - Energy Plants for Electricity and District heating generation (V0009). Danish Energy Agency
| Technology | Heat pumps utilizing industrial waste heat 3 MW
|  | 2020 | 2025 | 2030 | 2040 | 2050 | Uncertainty (2025) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data | [5 empty] | Lower | Upper | Lower | Upper
| Heat generation capacity for one unit (MJ/s) | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Total efficiency, net (%), name plate | 450 | 460 | 470 | 480 | 490 | 440 | 480 | 450 | 510 | A, A1, B, D | 1;14;15
| Total efficiency , net (%), annual average | 460 | 470 | 480 | 490 | 500 | 450 | 490 | 460 | 520 | A, A1, C, D | 1;14;15
| Auxiliary electricity consumption (% of heat gen) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | D | 1;14;15
| Forced outage (%) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 |  | 1;14;15
| Planned outage (weeks per year) | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | 1;14;15
| Technical lifetime (years) | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | 1;9;10;14;15
| Construction time (years) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | E, F | 9;14;15
| Space requirements (1000m2 per MWheat) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.1 | 0.03 | 0.1 |  | 15;18
Regulation ability
| Primary regulation (% per 30 seconds) | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 5 | 50 | G | 1;9;14;15
| Secondary regulation (% per minute) | 10 | 10 | 10 | 10 | 10 | 10 | 100 | 10 | 100 | G | 1;9;14;15
| Minimum load (% of full load) | 25 | 25 | 25 | 25 | 25 | 10 | 50 | 10 | 50 | G, I | 1;9;14;15
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | 9;14;15
| Cold start-up time (hours) | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | G, H | 9;14;15
Environment
SO2 (degree of desulphurization, %)
NOX (g per GJ fuel)
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Particles (g per GJ fuel)
Financial data
| Specific investment (M€ per MJ/s) | 0.85625 | 0.85625 | 0.76111 | 0.76111 | 0.76111 | 0.66597 | 1.1417 | 0.66597 | 1.1417 | A,J,K,O | 1;14;15
| - of which equipment | 0.685 | 0.685 | 0.60889 | 0.60889 | 0.60889 | 0.53278 | 0.91333 | 0.53278 | 0.91333 | A | 1;14;15
| - of which installation | 0.15412 | 0.15412 | 0.137 | 0.137 | 0.137 | 0.11987 | 0.11417 | 0.11987 | 0.11417 | A | 1;14;15
| - of which grid connection | 0.017125 | 0.017125 | 0.015222 | 0.015222 | 0.015222 | 0.013319 | 0.11417 | 0.013319 | 0.11417 | J | 1;14;15
| Fixed O&M (€/MJ/s/year) | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | 1;14;15
| Variable O&M (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 |  | 1;14;15
| - of which is electricity costs (€/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D,M | 1;14;15
| - of which is other O&M costs (€/MWh) | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 | L | 1;14;15
| Startup cost (€/MJ/s/startup) | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Technology specific data
Notes
A | Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1 | Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B | Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C | Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D | Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E | Does not include tendering and regulatory approvals.
F | The development within construction time will depend on future production figures and standardization of plants.
G | The regulation ability will depend on the future marktes for regulation services.
H | Cold start of time is starting a heat pump where stand by heating has not been applied
I | Operation at part load will usually increase COP but also variable O&M costs
J | It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K | Land is usually owned by the company
L | O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M | All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N | 1/4 MWh-heat per MW is lost during startup
O | At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
References
1 | Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2 | Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3 | Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4 | Scandinavian Energy Group, 2015, Conversation
5 | Advansor, 2015, Conversation
6 | Hybrid Energi, 2015, Conversation
7 | Innoterm, 2015, Conversation
8 | Cronborg, 2015, Conversation
9 | Johnson Controls, 2019, Conversation
10 | Teknologisk Institut, 2015, 2019, Conversation
11 | Energinet.dk, 2015, Conversation
12 | IEA 2012, Energy Technology Perspectives, 2012
13 | Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14 | IES/Victor DST, 2019, Conversation
15 | PlanEnergi, 2019, practical experience from installed plants
16 | DMI, 2019
17 | Danfoss, 2019, Conversation
18 | Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## HE_data
Source: Technology Data for heating installations (V0002). Danish Energy Agency
Technology |  | Indirect district heating substation - apartment complex - existing building
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Heat production capacity for one unit [kW_h] | 400 | 400 | 400 | 400 | 400 | 150 | 500 | 150 | 500 | A, H
Expected share of space heating demand covered by unit [p.u.] | bar: ctrl to upper
Expected share of hot tap water demand covered by unit [p.u.] | bar: ctrl to upper
| Heat efficiency (annual average, net) [p.u.] | 1 | 1 | 1 | 1 | 1 | 0.98 | 1 | 0.98 | 1 | B, I
| Auxiliary Electricity consumption [kWh_e/y] | 600 | 550 | 500 | 450 | 400 | 400 | 1000 | 250 | 800 | G
| Technical economic lifetime [years] | 25 | 25 | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 8
Electric regulation ability
Primary regulation (per 30 seconds) [p.u.]
Secondary regulation (per minute) [p.u.]
Minimum load (of full load) [p.u.]
Warm start-up time [hours]
Cold start-up time [hours]
Environment
SO2 [g/GJ_i]
PM2.5 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Financial data
| Nominal investment (*total) [k€/unit, 2020] | 16.56 | 16.1501 | 15.7504 | 14.9803 | 14.248 | 13.7276 | 19.3801 | 12.1108 | 17.0976 | F | 2, 4, 7, 10
| Nominal investment (equipment) [k€/unit, 2020] | 11.592 | 11.3051 | 11.0253 | 10.4862 | 9.9736 | 9.6093 | 13.5661 | 8.4775 | 11.9683
| Nominal investment (installation) [k€/unit, 2020] | 4.968 | 4.845 | 4.7251 | 4.4941 | 4.2744 | 4.1183 | 5.814 | 3.6332 | 5.1293
| Nominal investment (additional) [k€/unit, 2020] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | C, E
| Fixed O&M (*total) [€/unit/y, 2020] | 140.4 | 143.25 | 144.5 | 138.55 | 131.8 | 110.5 | 201.5 | 94.25 | 198.6 | D
| Fixed O&M (electricity cost) [€/unit/y, 2020] | 41.4 | 46.75 | 50.5 | 49.05 | 46.8 | 34 | 85 | 29.25 | 93.6
| Fixed O&M (other) [€/unit/y, 2020] | 99 | 96.5 | 94 | 89.5 | 85 | 76.5 | 116.5 | 65 | 105
| Annual O&M (time spent on manual maintenance) [hours/unit/y] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
References:
2. Communication with Gemina Termix, www.termix.dk. 2011
4. Communication with Danfoss Redan, www.redan.danfoss.com. Technology data for individual heat production and energy transport, 2011
7. Prices from different providers of substations, 2016
8. Analysis conducted by COWI on the lifetime and operation and maintenance costs of district heating units, 2016
10. Interview with market actors and web price survey, 2020
Notes:
A. The generating capacity for one substation is set at the space heating capacity at typical district heating flow/return temperatures of 70°C/40°C. The size of the water heater capacity is estimated based on the number of apartments that the substation can supply with space heating.
B. The only losses related to the district heating substation are the standby heat losses and system losses related to the cooling of the return flow. For large well-insulated substations, these are considered negligible – 100% efficiency. However, substations for single-family houses will have a heat loss during summer that cannot be considered useful. Applying best available technology, this is considered to be about 3%, resulting in 97% efficiency.
C. Specific investment in branch pipe from the steet network to the building and in the heat meter. Lifetime for the branchpipe is estimated to be 50 years.
D. The operation and maintenance costs are based on a maintenance check every second year, but calculated per year and per installation.
E. Note that the branch pipe should be dimensioned for the use of hot tap water. If there is not any hot water tank, the branch pipe capacity should be higher than the capacity of the DH substation.
F. Assuming a cost-reduction of 0.5 % p.a., which in turn is assumed equivalent to the typical improvement of mature technologies.
G. The cost of auxiliary electricity consumption is calculated using the following electricity prices in €/MWh: 2020: 69, 2025: 85, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
H. Due to the insignificant economy of scale displayed by domestic district heating substations (se section on economy of scale) the savings achieved by reducing the capacity of the substation is limited or non-existing. Hence, the investment cost is not influenced by the capacity of the substations installed.
I. In contrast to boilers and heat pumps a district heating unit does not convert energy. Yet energy losses are still present in a district heating substation [9]. Some of these losses are included in the annual heat demand, while others are not. The efficiencies are calculated to reflect this.