## Cover
TIMES-Ireland Model
Document type: | Scenario
Sector(s): | All
Purpose: | Specify unit commitment parameters
Original developer(s): | Xiufeng Yue (UCC, xiufeng.yue@ucc.ie)
Current maintainer(s): | Olexandr Balyk (UCC, olexandr.balyk@ucc.ie)
Part of TIM version: | 1
Model repository: | https://github.com/MaREI-EPMG/TIMES-Ireland-model
Licence: | CC BY-NC-SA 4.0 (unless specified otherwise)
https://creativecommons.org/licenses/by-nc-sa/4.0/

## CSTSD
Start-up costs
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS* | HOT | ACT_CSTSD | UP | 0.026 | 26
Gas OCGT | P*OCGT-GAS* | HOT | ACT_CSTSD | UP | 0.024 | 24
Coal SC | P*SC-COA*,P*SC-PEA* | HOT | ACT_CSTSD | UP | 0.04 | 40
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA* | HOT | ACT_CSTSD | UP | 0.07 | 70
Oil | P*HFO*,P*DIS* | HOT | ACT_CSTSD | UP | 0
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS* | WARM | ACT_CSTSD | UP | 0.041 | 41
Gas OCGT | P*OCGT-GAS* | WARM | ACT_CSTSD | UP | 0.0945 | 94.5
Coal SC | P*SC-COA*,P*SC-PEA* | WARM | ACT_CSTSD | UP | 0.048 | 48
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA* | WARM | ACT_CSTSD | UP | 0.117 | 117
Oil | P*HFO*,P*DIS* | WARM | ACT_CSTSD | UP | 0
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS* | COLD | ACT_CSTSD | UP | 0.059 | 59
Gas OCGT | P*OCGT-GAS* | COLD | ACT_CSTSD | UP | 0.077 | 77
Coal SC | P*SC-COA*,P*SC-PEA* | COLD | ACT_CSTSD | UP | 0.078 | 78
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA* | COLD | ACT_CSTSD | UP | 0.11 | 110
Oil | P*HFO*,P*DIS* | COLD | ACT_CSTSD | UP | 0

## LOSSD
Fuel increase during Start-up and Shut-down phase
~TFM_INS
Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Source: TIMES Manual
P*TH*0* | HOT | ACT_LOSSD | LO | 1.3
P*TH*0* | HOT | ACT_LOSSD | UP | 1.2
P*TH*0* | WARM | ACT_LOSSD | UP | 1.4
P*TH*0* | COLD | ACT_LOSSD | UP | 1.6

## SDTIME
Start-up and Shut-down time
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
| P*TH*0* | HOT | ACT_SDTIME | LO | 3
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* | HOT | ACT_SDTIME | UP | 4
Gas OCGT | P*OCGT-GAS*,-P-TH*00* | HOT | ACT_SDTIME | UP | 0
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* | HOT | ACT_SDTIME | UP | 6
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* | HOT | ACT_SDTIME | UP | 6
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* | WARM | ACT_TIME | UP | 2
Gas OCGT | P*OCGT-GAS*,-P-TH*00* | WARM | ACT_TIME | UP | 0
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* | WARM | ACT_TIME | UP | 4
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* | WARM | ACT_TIME | UP | 6
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* | COLD | ACT_TIME | UP | 2
Gas OCGT | P*OCGT-GAS*,-P-TH*00* | COLD | ACT_TIME | UP | 0
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* | COLD | ACT_TIME | UP | 4
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* | COLD | ACT_TIME | UP | 6

## UPS
Ramp up/down rate (%capacity per hour)
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
| P*TH*0* |  | ACT_UPS | LO | 0.4
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* |  | ACT_UPS | UP | 0.498
Gas OCGT | P*OCGT-GAS*,-P-TH*00* |  | ACT_UPS | UP | 0.348
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* |  | ACT_UPS | UP | 0.498
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* |  | ACT_UPS | UP | 0.348

## LOSPL
proportional increase in specific fuel consumption at the minimum operating level
~TFM_INS
Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Source: TIMES Manual
P*TH*0*,-P*TH*00* |  | ACT_LOSPL | UP | 0.68
P*TH*0* |  | ACT_LOSPL | FX | 0.2

## MINLD
Minimum Statble load level (% Capacity)
~TFM_INS
Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
P*TH*0*,-P-TH*00* |  | ACT_MINLD |  | 0.4

## TIME
Minimum up/downtime
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* |  | ACT_TIME | UP | 4
Gas OCGT | P*OCGT-GAS*,-P-TH*00* |  | ACT_TIME | UP | 0
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* |  | ACT_TIME | UP | 6
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* |  | ACT_TIME | UP | 6
~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
Gas CCGT | P*CCGT-GAS*,-P-TH*00* |  | ACT_TIME | LO | 2
Gas OCGT | P*OCGT-GAS*,-P-TH*00* |  | ACT_TIME | LO | 0
Coal SC | P*SC-COA*,P*SC-PEA*,-P-TH*00* |  | ACT_TIME | LO | 4
Coal Old | P*COA*,P*PEA*,-P*SC-COA*,-P*SC-PEA*,-P-TH*00* |  | ACT_TIME | LO | 6

## MAXON
Transition Boundary from HOT-WARM-COLD
~TFM_INS
Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Source:Schröder, Andreas; Kunz, Friedrich; Meiss, Jan; Mendelevitch, Roman; von Hirschhausen, Christian (2013) : Current and prospective costs of electricity generation until 2050, DIW Data Documentation, No. 68, Deutsches Institut für Wirtschaftsforschung (DIW), Berlin
P*TH*0* | HOT | ACT_MAXNON |  | 8
P*TH*0* | WARM | ACT_MAXNON |  | 50

## UC_SEM_PLEXOS
| ~TFM_INS |  |  |  |  | ~TFM_INS |  |  |  |  | ~TFM_INS |  |  |  |  | ~TFM_INS |  |  |  |  | ~TFM_INS
| Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Pset_PN | Other_Indexes | Attribute | LimType | AllRegions | Pset_PN | Other_Indexes | Attribute | LimType | AllRegions
ADC | P-TH-CCGT-GAS00-ADC |  | ACT_MINLD |  | 0.48649 | P-TH-CCGT-GAS00-ADC |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-ADC |  | ACT_TIME | LO | 1 | P-TH-CCGT-GAS00-ADC |  | ACT_UPS | UP | 1.1932 | P-TH-CCGT-GAS00-ADC |  | ACT_UPS | LO | 1.673
AT1 | P-TH-OCGT-GAS00-AT1 |  | ACT_MINLD |  | 0.16667 | P-TH-OCGT-GAS00-AT1 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-AT1 |  | ACT_TIME | LO | 1 | P-TH-OCGT-GAS00-AT1 |  | ACT_UPS | UP | 3.3333 | P-TH-OCGT-GAS00-AT1 |  | ACT_UPS | LO | 3.3333
AT2 | P-TH-OCGT-GAS00-AT2 |  | ACT_MINLD |  | 0.16667 | P-TH-OCGT-GAS00-AT2 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-AT2 |  | ACT_TIME | LO | 1 | P-TH-OCGT-GAS00-AT2 |  | ACT_UPS | UP | 3.3333 | P-TH-OCGT-GAS00-AT2 |  | ACT_UPS | LO | 3.3333
AT4 | P-TH-OCGT-GAS00-AT4 |  | ACT_MINLD |  | 0.16667 | P-TH-OCGT-GAS00-AT4 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-AT4 |  | ACT_TIME | LO | 1 | P-TH-OCGT-GAS00-AT4 |  | ACT_UPS | UP | 3.3333 | P-TH-OCGT-GAS00-AT4 |  | ACT_UPS | LO | 3.3333
B10 | P-TH-CCGT-GAS00-B10 |  | ACT_MINLD |  | 0.62376 | P-TH-CCGT-GAS00-B10 |  | ACT_TIME | UP | 0.02 | P-TH-CCGT-GAS00-B10 |  | ACT_TIME | LO | 0.25 | P-TH-CCGT-GAS00-B10 |  | ACT_UPS | UP | 0.6297 | P-TH-CCGT-GAS00-B10 |  | ACT_UPS | LO | 2.3644
B31 | P-TH-CCGT-GAS00-B31 |  | ACT_MINLD |  | 0.45749 | P-TH-CCGT-GAS00-B31 |  | ACT_TIME | UP | 0.02 | P-TH-CCGT-GAS00-B31 |  | ACT_TIME | LO | 0.25 | P-TH-CCGT-GAS00-B31 |  | ACT_UPS | UP | 2.6721 | P-TH-CCGT-GAS00-B31 |  | ACT_UPS | LO | 2.6721
B32 | P-TH-CCGT-GAS00-B32 |  | ACT_MINLD |  | 0.45749 | P-TH-CCGT-GAS00-B32 |  | ACT_TIME | UP | 0.02 | P-TH-CCGT-GAS00-B32 |  | ACT_TIME | LO | 0.25 | P-TH-CCGT-GAS00-B32 |  | ACT_UPS | UP | 2.6721 | P-TH-CCGT-GAS00-B32 |  | ACT_UPS | LO | 2.6721
BGT1 | P-TH-OCGT-DIS00-BGT1 |  | ACT_MINLD |  | 0.13793 | P-TH-OCGT-DIS00-BGT1 |  | ACT_TIME | UP | 0.02 | P-TH-OCGT-DIS00-BGT1 |  | ACT_TIME | LO | 0.25 | P-TH-OCGT-DIS00-BGT1 |  | ACT_UPS | UP | 5.1724 | P-TH-OCGT-DIS00-BGT1 |  | ACT_UPS | LO | 6.6517
BGT2 | P-TH-OCGT-DIS00-BGT2 |  | ACT_MINLD |  | 0.13793 | P-TH-OCGT-DIS00-BGT2 |  | ACT_TIME | UP | 0.02 | P-TH-OCGT-DIS00-BGT2 |  | ACT_TIME | LO | 0.25 | P-TH-OCGT-DIS00-BGT2 |  | ACT_UPS | UP | 5.1724 | P-TH-OCGT-DIS00-BGT2 |  | ACT_UPS | LO | 6.6517
CGT8 | P-TH-OCGT-DIS00-CGT8 |  | ACT_MINLD |  | 0.15094 | P-TH-OCGT-DIS00-CGT8 |  | ACT_TIME | UP | 0.02 | P-TH-OCGT-DIS00-CGT8 |  | ACT_TIME | LO | 0.25 | P-TH-OCGT-DIS00-CGT8 |  | ACT_UPS | UP | 56.6038 | P-TH-OCGT-DIS00-CGT8 |  | ACT_UPS | LO | 56.6038
CGA | P-TH-OCGT-GAS00-CGA |  | ACT_MINLD |  | 0.49652 | P-TH-OCGT-GAS00-CGA |  | ACT_TIME | UP | 0.5 | P-TH-OCGT-GAS00-CGA |  | ACT_TIME | LO | 0.5 | P-TH-OCGT-GAS00-CGA |  | ACT_UPS | UP | 20.0199 | P-TH-OCGT-GAS00-CGA |  | ACT_UPS | LO | 20.0199
CPS | P-TH-CCGT-GAS00-CPS |  | ACT_MINLD |  | 0.63107 | P-TH-CCGT-GAS00-CPS |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-CPS |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-CPS |  | ACT_UPS | UP | 2.1845 | P-TH-CCGT-GAS00-CPS |  | ACT_UPS | LO | 1.216
DB1 | P-TH-CCGT-GAS00-DB1 |  | ACT_MINLD |  | 0.47991 | P-TH-CCGT-GAS00-DB1 |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-DB1 |  | ACT_TIME | LO | 1 | P-TH-CCGT-GAS00-DB1 |  | ACT_UPS | UP | 1.4184 | P-TH-CCGT-GAS00-DB1 |  | ACT_UPS | LO | 1.2766
ED1 | P-TH-ST-PEA00-ED1 |  | ACT_MINLD |  | 0.34864 | P-TH-ST-PEA00-ED1 |  | ACT_TIME | UP | 4 | P-TH-ST-PEA00-ED1 |  | ACT_TIME | LO | 0.5 | P-TH-ST-PEA00-ED1 |  | ACT_UPS | UP | 0.89796 | P-TH-ST-PEA00-ED1 |  | ACT_UPS | LO | 0.89796
ED3 | P-TH-OCGT-DIS00-ED3 |  | ACT_MINLD |  | 0.34483 | P-TH-OCGT-DIS00-ED3 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-ED3 |  | ACT_TIME | LO | 0.5 | P-TH-OCGT-DIS00-ED3 |  | ACT_UPS | UP | 5.1724 | P-TH-OCGT-DIS00-ED3 |  | ACT_UPS | LO | 5.1724
ED5 | P-TH-OCGT-DIS00-ED5 |  | ACT_MINLD |  | 0.34483 | P-TH-OCGT-DIS00-ED5 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-ED5 |  | ACT_TIME | LO | 0.5 | P-TH-OCGT-DIS00-ED5 |  | ACT_UPS | UP | 5.1724 | P-TH-OCGT-DIS00-ED5 |  | ACT_UPS | LO | 5.1724
GI | P-TH-CCGT-GAS00-GI |  | ACT_MINLD |  | 0.3556 | P-TH-CCGT-GAS00-GI |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-GI |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-GI |  | ACT_UPS | UP | 2.2203 | P-TH-CCGT-GAS00-GI |  | ACT_UPS | LO | 2.3922
HN2 | P-TH-CCGT-GAS00-HN2 |  | ACT_MINLD |  | 0.2995 | P-TH-CCGT-GAS00-HN2 |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-HN2 |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-HN2 |  | ACT_UPS | UP | 2.9703 | P-TH-CCGT-GAS00-HN2 |  | ACT_UPS | LO | 2.9703
HNC | P-TH-CCGT-GAS00-HNC |  | ACT_MINLD |  | 0.34985 | P-TH-CCGT-GAS00-HNC |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-HNC |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-HNC |  | ACT_UPS | UP | 1.2245 | P-TH-CCGT-GAS00-HNC |  | ACT_UPS | LO | 1.2245
AGU | P-TH-CCGT-DIS00-AGU |  | ACT_MINLD |  | 34% | P-TH-CCGT-DIS00-AGU |  | ACT_TIME | UP | 0.5 | P-TH-CCGT-DIS00-AGU |  | ACT_TIME | LO | 0.5 | P-TH-CCGT-DIS00-AGU |  | ACT_UPS | UP | 7.5 | P-TH-CCGT-DIS00-AGU |  | ACT_UPS | LO | 7.5
K1 | P-TH-ST-COA00-K1 |  | ACT_MINLD |  | 0.36471 | P-TH-ST-COA00-K1 |  | ACT_TIME | UP | 4 | P-TH-ST-COA00-K1 |  | ACT_TIME | LO | 0.5 | P-TH-ST-COA00-K1 |  | ACT_UPS | UP | 1.3624 | P-TH-ST-COA00-K1 |  | ACT_UPS | LO | 1.3624
K2 | P-TH-ST-COA00-K2 |  | ACT_MINLD |  | 0.36047 | P-TH-ST-COA00-K2 |  | ACT_TIME | UP | 4 | P-TH-ST-COA00-K2 |  | ACT_TIME | LO | 0.5 | P-TH-ST-COA00-K2 |  | ACT_UPS | UP | 1.3465 | P-TH-ST-COA00-K2 |  | ACT_UPS | LO | 1.3465
KGT1 | P-TH-OCGT-DIS00-KGT1 |  | ACT_MINLD |  | 0.17241 | P-TH-OCGT-DIS00-KGT1 |  | ACT_TIME | UP | 0.02 | P-TH-OCGT-DIS00-KGT1 |  | ACT_TIME | LO | 0.25 | P-TH-OCGT-DIS00-KGT1 |  | ACT_UPS | UP | 5.5241 | P-TH-OCGT-DIS00-KGT1 |  | ACT_UPS | LO | 5.5241
KGT2 | P-TH-OCGT-DIS00-KGT2 |  | ACT_MINLD |  | 0.17241 | P-TH-OCGT-DIS00-KGT2 |  | ACT_TIME | UP | 0.02 | P-TH-OCGT-DIS00-KGT2 |  | ACT_TIME | LO | 0.25 | P-TH-OCGT-DIS00-KGT2 |  | ACT_UPS | UP | 5.5241 | P-TH-OCGT-DIS00-KGT2 |  | ACT_UPS | LO | 5.5241
KGT3 | P-TH-OCGT-DIS00-KGT3 |  | ACT_MINLD |  | 0.30522 | P-TH-OCGT-DIS00-KGT3 |  | ACT_TIME | UP | 0.62 | P-TH-OCGT-DIS00-KGT3 |  | ACT_TIME | LO | 0.38 | P-TH-OCGT-DIS00-KGT3 |  | ACT_UPS | UP | 14.2857 | P-TH-OCGT-DIS00-KGT3 |  | ACT_UPS | LO | 14.2857
KGT4 | P-TH-OCGT-DIS00-KGT4 |  | ACT_MINLD |  | 0.30522 | P-TH-OCGT-DIS00-KGT4 |  | ACT_TIME | UP | 0.62 | P-TH-OCGT-DIS00-KGT4 |  | ACT_TIME | LO | 0.38 | P-TH-OCGT-DIS00-KGT4 |  | ACT_UPS | UP | 14.2857 | P-TH-OCGT-DIS00-KGT4 |  | ACT_UPS | LO | 14.2857
LR4 | P-TH-ST-PEA00-LR4 |  | ACT_MINLD |  | 0.97849 | P-TH-ST-PEA00-LR4 |  | ACT_TIME | UP | 4 | P-TH-ST-PEA00-LR4 |  | ACT_TIME | LO | 4 | P-TH-ST-PEA00-LR4 |  | ACT_UPS | UP | 0.32258 | P-TH-ST-PEA00-LR4 |  | ACT_UPS | LO | 0.32258
MP1 | P-TH-ST-COA00-MP1 |  | ACT_MINLD |  | 0.34737 | P-TH-ST-COA00-MP1 |  | ACT_TIME | UP | 6 | P-TH-ST-COA00-MP1 |  | ACT_TIME | LO | 5 | P-TH-ST-COA00-MP1 |  | ACT_UPS | UP | 0.34316 | P-TH-ST-COA00-MP1 |  | ACT_UPS | LO | 0.95579
MP2 | P-TH-ST-COA00-MP2 |  | ACT_MINLD |  | 0.34737 | P-TH-ST-COA00-MP2 |  | ACT_TIME | UP | 6 | P-TH-ST-COA00-MP2 |  | ACT_TIME | LO | 5 | P-TH-ST-COA00-MP2 |  | ACT_UPS | UP | 0.34316 | P-TH-ST-COA00-MP2 |  | ACT_UPS | LO | 0.94526
MP3 | P-TH-ST-COA00-MP3 |  | ACT_MINLD |  | 0.34737 | P-TH-ST-COA00-MP3 |  | ACT_TIME | UP | 6 | P-TH-ST-COA00-MP3 |  | ACT_TIME | LO | 5 | P-TH-ST-COA00-MP3 |  | ACT_UPS | UP | 0.34316 | P-TH-ST-COA00-MP3 |  | ACT_UPS | LO | 0.95579
NW5 | P-TH-OCGT-GAS00-NW5 |  | ACT_MINLD |  | 0.036789 | P-TH-OCGT-GAS00-NW5 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-NW5 |  | ACT_TIME | LO | 0.5 | P-TH-OCGT-GAS00-NW5 |  | ACT_UPS | UP | 4.4037 | P-TH-OCGT-GAS00-NW5 |  | ACT_UPS | LO | 4.4037
PBA | P-TH-CCGT-GAS00-PBA |  | ACT_MINLD |  | 0.46875 | P-TH-CCGT-GAS00-PBA |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-PBA |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-PBA |  | ACT_UPS | UP | 2.5781 | P-TH-CCGT-GAS00-PBA |  | ACT_UPS | LO | 2.5781
PBB | P-TH-CCGT-GAS00-PBB |  | ACT_MINLD |  | 0.46875 | P-TH-CCGT-GAS00-PBB |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-PBB |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-PBB |  | ACT_UPS | UP | 2.5781 | P-TH-CCGT-GAS00-PBB |  | ACT_UPS | LO | 2.5781
RH1 | P-TH-OCGT-DIS00-RH1 |  | ACT_MINLD |  | 0.096154 | P-TH-OCGT-DIS00-RH1 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-RH1 |  | ACT_TIME | LO | 0.75 | P-TH-OCGT-DIS00-RH1 |  | ACT_UPS | UP | 11.5385 | P-TH-OCGT-DIS00-RH1 |  | ACT_UPS | LO | 11.5385
RH2 | P-TH-OCGT-DIS00-RH2 |  | ACT_MINLD |  | 0.096154 | P-TH-OCGT-DIS00-RH2 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-RH2 |  | ACT_TIME | LO | 0.75 | P-TH-OCGT-DIS00-RH2 |  | ACT_UPS | UP | 11.5385 | P-TH-OCGT-DIS00-RH2 |  | ACT_UPS | LO | 11.5385
SK3 | P-TH-OCGT-GAS00-SK3 |  | ACT_MINLD |  | 0.48193 | P-TH-OCGT-GAS00-SK3 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-SK3 |  | ACT_TIME | LO | 4 | P-TH-OCGT-GAS00-SK3 |  | ACT_UPS | UP | 4.3373 | P-TH-OCGT-GAS00-SK3 |  | ACT_UPS | LO | 4.3373
SK4 | P-TH-OCGT-GAS00-SK4 |  | ACT_MINLD |  | 0.48193 | P-TH-OCGT-GAS00-SK4 |  | ACT_TIME | UP | 4 | P-TH-OCGT-GAS00-SK4 |  | ACT_TIME | LO | 4 | P-TH-OCGT-GAS00-SK4 |  | ACT_UPS | UP | 4.3373 | P-TH-OCGT-GAS00-SK4 |  | ACT_UPS | LO | 4.3373
TB1 | P-TH-ST-HFO00-TB1 |  | ACT_MINLD |  | 0.33333 | P-TH-ST-HFO00-TB1 |  | ACT_TIME | UP | 2 | P-TH-ST-HFO00-TB1 |  | ACT_TIME | LO | 2 | P-TH-ST-HFO00-TB1 |  | ACT_UPS | UP | 1.1111 | P-TH-ST-HFO00-TB1 |  | ACT_UPS | LO | 1.1111
TB2 | P-TH-ST-HFO00-TB2 |  | ACT_MINLD |  | 0.33333 | P-TH-ST-HFO00-TB2 |  | ACT_TIME | UP | 2 | P-TH-ST-HFO00-TB2 |  | ACT_TIME | LO | 2 | P-TH-ST-HFO00-TB2 |  | ACT_UPS | UP | 1.1111 | P-TH-ST-HFO00-TB2 |  | ACT_UPS | LO | 1.1111
TB3 | P-TH-ST-HFO00-TB3 |  | ACT_MINLD |  | 0.14342 | P-TH-ST-HFO00-TB3 |  | ACT_TIME | UP | 4 | P-TH-ST-HFO00-TB3 |  | ACT_TIME | LO | 4 | P-TH-ST-HFO00-TB3 |  | ACT_UPS | UP | 0.49383 | P-TH-ST-HFO00-TB3 |  | ACT_UPS | LO | 0.54321
TB4 | P-TH-ST-HFO00-TB4 |  | ACT_MINLD |  | 0.14342 | P-TH-ST-HFO00-TB4 |  | ACT_TIME | UP | 4 | P-TH-ST-HFO00-TB4 |  | ACT_TIME | LO | 4 | P-TH-ST-HFO00-TB4 |  | ACT_UPS | UP | 0.49383 | P-TH-ST-HFO00-TB4 |  | ACT_UPS | LO | 0.54321
TP1 | P-TH-OCGT-DIS00-TP1 |  | ACT_MINLD |  | 0.096154 | P-TH-OCGT-DIS00-TP1 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-TP1 |  | ACT_TIME | LO | 0.75 | P-TH-OCGT-DIS00-TP1 |  | ACT_UPS | UP | 11.5385 | P-TH-OCGT-DIS00-TP1 |  | ACT_UPS | LO | 11.5385
TP3 | P-TH-OCGT-DIS00-TP3 |  | ACT_MINLD |  | 0.096154 | P-TH-OCGT-DIS00-TP3 |  | ACT_TIME | UP | 0 | P-TH-OCGT-DIS00-TP3 |  | ACT_TIME | LO | 0.75 | P-TH-OCGT-DIS00-TP3 |  | ACT_UPS | UP | 11.5385 | P-TH-OCGT-DIS00-TP3 |  | ACT_UPS | LO | 11.5385
TY | P-TH-CCGT-GAS00-TY |  | ACT_MINLD |  | 0.4802 | P-TH-CCGT-GAS00-TY |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-TY |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-TY |  | ACT_UPS | UP | 2.2277 | P-TH-CCGT-GAS00-TY |  | ACT_UPS | LO | 1.8564
WG | P-TH-CCGT-GAS00-WG |  | ACT_MINLD |  | 0.40449 | P-TH-CCGT-GAS00-WG |  | ACT_TIME | UP | 4 | P-TH-CCGT-GAS00-WG |  | ACT_TIME | LO | 4 | P-TH-CCGT-GAS00-WG |  | ACT_UPS | UP | 2.7775 | P-TH-CCGT-GAS00-WG |  | ACT_UPS | LO | 3.6135
WO4 | P-TH-ST-PEA00-WO4 |  | ACT_MINLD |  | 0.97857 | P-TH-ST-PEA00-WO4 |  | ACT_TIME | UP | 4 | P-TH-ST-PEA00-WO4 |  | ACT_TIME | LO | 4 | P-TH-ST-PEA00-WO4 |  | ACT_UPS | UP | 0.3 | P-TH-ST-PEA00-WO4 |  | ACT_UPS | LO | 0.3

## Data_SEM_PLEXOS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36
Data Source:SEM-PLEXOS | [33 empty] | Min Up Time (hrs) | Min Down Time (hrs)
TIMES ID | Efficiency | Plant ID | [5 empty] | Fuel type |  |  |  |  | Capacity |  |  |  | Heat Rate Curve | [10 empty] | Forced Outages |  | TOD
|  | Company Name | Jurisdiction | SEM Unit ID | PLEXOS Unit ID | Unit Name | Change Date for New Unit Characteristics | Start Fuel 1 | Percent 1 | Start Fuel 2 | Percent 2 | Fuel for Generation and No Load | Min Stable Capacity (MW) | Max Capacity (MW) | Summer Rating--Where Different (MW) | ACT_MINLD | No Load Heat Requirement (GJ/hr) | Capacity point 1 (MW) | Capacity point 2 (MW) | Capacity point 3 (MW) | Capacity point 4 (MW) | Capacity point 5 (MW) | Heat Rate Inc 1 (GJ/MWh) | Heat Rate Inc 2 (GJ/MWh) | Heat Rate Inc 3 (GJ/MWh) | Heat Rate Inc 4 (GJ/MWh) | Heat Rate Inc 5 (GJ/MWh) | Forced Outage Rate,% | Mean Time to Repair, hrs | Ramp Rate Up, MW/min | ACT_UPS_UP | Ramp Rate Down, MW/min | ACT_UPS_LO | ACT_TIME_UP | ACT_TIME_LO
MP1 | 0.33657 | ESB | ROI | GU_400270 | MP1 | Moneypoint 1 |  | Coal | 0.68 | Gasoil | 0.32 | Coal | 99 | 285 |  | 34.74% | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 9.1% | 284 | 1.63 | 0.34316 | 4.54 | 0.95579 | 6 | 5
MP2 | 0.33657 | ESB | ROI | GU_400271 | MP2 | Moneypoint 2 |  | Coal | 0.68 | Gasoil | 0.32 | Coal | 99 | 285 |  | 34.74% | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 9.1% | 283 | 1.63 | 0.34316 | 4.49 | 0.94526 | 6 | 5
MP3 | 0.33657 | ESB | ROI | GU_400272 | MP3 | Moneypoint 3 |  | Coal | 0.68 | Gasoil | 0.32 | Coal | 99 | 285 |  | 34.74% | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 9.1% | 284 | 1.63 | 0.34316 | 4.54 | 0.95579 | 6 | 5
K1 | 0.18118 | AES | NI | GU_500822 | K1 Coal 220 | Kilroot Unit 1 FGD |  | Oil | 0.8 | Coal | 0.2 | Coal | 93 | 255 |  | 36.47% | 393.605 | 93 | 174.8 | 199 | 237.6 |  | 9.4 | 9.4 | 9.4 | 51.28 |  | 9.1% | 24 | 5.79 | 1.3624 | 5.79 | 1.3624 | 4 | 0.5
K2 | 0.18118 | AES | NI | GU_500823 | K2 Coal 220 | Kilroot Unit 2 FGD |  | Oil | 0.8 | Coal | 0.2 | Coal | 93 | 258 |  | 36.05% | 393.605 | 93 | 174.8 | 199 | 237.6 |  | 9.4 | 9.4 | 9.4 | 51.28 |  | 9.1% | 24 | 5.79 | 1.3465 | 5.79 | 1.3465 | 4 | 0.5
AD1 | 0.42461 | ESB | ROI | GU_400180 | AD1 | Aghada 1 |  | Gas | 1 |  |  | Gas | 36 | 258 |  | 13.95% | 187.432 | 120 | 190 | 258 |  |  | 8.013 | 8.674 | 8.748 |  |  | 6.2% | 480 | 3.87 | 0.9 | 3.86 | 0.89767 | 4 | 3.5
ADC | 0.6972 | ESB | ROI | GU_400850 | ADC | Aghada CCGT |  | Gas | 1 |  |  | Gas | 216 | 444 | 439 | 48.65% | 589.4 | 220 | 430 | 440 | 444 |  | 4.24 | 5.364 | 5.525 | 5.525 |  | 6.2% | 192 | 8.83 | 1.1932 | 12.38 | 1.673 | 4 | 1
AT1 | 0.41664 | ESB | ROI | GU_400181 | AT1 | Aghada CT 1 |  | Gas | 1 |  |  | Gas | 15 | 90 |  | 16.67% | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 6.2% | 174 | 5 | 3.3333 | 5 | 3.3333 | 4 | 1
AT2 | 0.41664 | ESB | ROI | GU_400182 | AT2 | Aghada CT 2 |  | Gas | 1 |  |  | Gas | 15 | 90 |  | 16.67% | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 6.2% | 174 | 5 | 3.3333 | 5 | 3.3333 | 4 | 1
AT4 | 0.41664 | ESB | ROI | GU_400183 | AT4 | Aghada CT 4 |  | Gas | 1 |  |  | Gas | 15 | 90 |  | 16.67% | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 6.2% | 174 | 5 | 3.3333 | 5 | 3.3333 | 4 | 1
B10 | 0.5997 | POWERNI | NI | GU_500140 | B10 | Ballylumford CCGT Unit 10 |  | Gas | 1 |  |  | Gas | 63 | 101 | 98.9 | 62.38% | 79.51 | 63 | 101 |  |  |  | 6.003 | 6.003 |  |  |  | 6.2% | 72 | 1.06 | 0.6297 | 3.98 | 2.3644 | 0.02 | 0.25
B31 | 0.62992 | POWERNI | NI | GU_500130 | B31 | Ballylumford CCGT Unit 31 |  | Gas | 1 |  |  | Gas | 113 | 247 | 244.1 | 45.75% | 315.9 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 2.6721 | 11 | 2.6721 | 0.02 | 0.25
B32 | 0.62992 | POWERNI | NI | GU_500131 | B32 | Ballylumford CCGT Unit 32 |  | Gas | 1 |  |  | Gas | 113 | 247 | 244.1 | 45.75% | 315.9 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 6.2% | 72 | 11 | 2.6721 | 11 | 2.6721 | 0.02 | 0.25
B4 | 0.31433 | AES | NI | GU_500282 | B4 | Ballylumford Unit 4 |  | Gas | 1 |  |  | Gas | 54 | 144 |  | 37.5% | 212.99 | 54 | 143.5 |  |  |  | 11.453 | 11.453 |  |  |  | 6.2% | 36 | 1.98 | 0.825 | 9.67 | 4.0292 | 2 | 1
B5 | 0.32418 | AES | NI | GU_500281 | B5 | Ballylumford Unit 5 |  | Gas | 1 |  |  | Gas | 54 | 147 |  | 36.73% | 210.01 | 54 | 146.5 |  |  |  | 11.105 | 11.105 |  |  |  | 6.2% | 36 | 1.98 | 0.80816 | 9.67 | 3.9469 | 2 | 1
CGA | 0.45147 | Contour | NI | GU_500904 | Contour AGU | Contour Global Agg Unit |  | Gas | 1 |  |  | Gas | 6 | 12.084 |  | 49.65% | 15.408 | 9 | 12 |  |  |  | 7.632 | 8.316 |  |  |  | 6.2% | 48 | 4.032 | 20.0199 | 4.032 | 20.0199 | 0.5 | 0.5
CPS | 0.67914 | ESB | NI | GU_500040 | CPS CCGT | Coolkeeragh CCGT |  | Gas | 1 |  |  | Gas | 260 | 412 |  | 63.11% | 633.76 | 260 | 328 | 372 | 404 | 412 | 4.384 | 5.341 | 5.573 | 5.603 | 5.603 | 6.2% | 176 | 15 | 2.1845 | 8.35 | 1.216 | 4 | 4
DB1 | 0.68392 | ESB | ROI | GU_400500 | DB1 | Dublin Bay CCGT |  | Gas | 1 |  |  | Gas | 203 | 423 | 415 | 47.99% | 594.7 | 203 | 405 | 415 | 416 |  | 4.018 | 5.679 | 5.679 | 5.679 |  | 6.2% | 176 | 10 | 1.4184 | 9 | 1.2766 | 4 | 1
GI | 0.71434 | SSE | ROI | GU_400762 | GI CCGT | Great Island CCGT |  | Gas | 1 |  |  | Gas | 165 | 464 | 458.5 | 35.56% | 605 | 203 | 320 | 464 |  |  | 4.0891 | 5.4069 | 5.6228 |  |  | 6.2% | 55 | 17.17 | 2.2203 | 18.5 | 2.3922 | 4 | 4
HN2 | 0.74514 | Viridian | ROI | GU_400540 | HN2 | Huntstown Phase II |  | Gas | 1 |  |  | Gas | 121 | 404 | 391.88 | 29.95% | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 6.2% | 55 | 20 | 2.9703 | 20 | 2.9703 | 4 | 4
HNC | 0.70365 | Viridian | ROI | GU_400480 | HNC | Huntstown |  | Gas | 1 |  |  | Gas | 120 | 343 | 332.71 | 34.99% | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 6.2% | 55 | 7 | 1.2245 | 7 | 1.2245 | 4 | 4
MRC | 0.36611 | ESB | ROI | GU_400300 | MRC | Marina |  | Gas | 1 |  |  | Gas | 45 | 95 |  | 47.37% | 258.4 | 47 | 81 | 95 |  |  | 8.644 | 9.462 | 11.393 |  |  | 6.2% | 72 | 5 | 3.1579 | 5 | 3.1579 | 1 | 0.5
NW5 | 0.40509 | ESB | ROI | GU_400311 | NW5 | North Wall 5 |  | Gas | 1 |  |  | Gas | 4.01 | 109 |  | 3.679% | 323.3 | 50 | 109 |  |  |  | 8.887 | 8.887 |  |  |  | 6.2% | 328 | 8 | 4.4037 | 8 | 4.4037 | 4 | 0.5
PBA | 0.58382 | ESB | ROI | GU_400324 | PBA | Poolbeg C_A |  | Gas | 1 |  |  | Gas | 120 | 256 |  | 46.88% | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 11 | 2.5781 | 11 | 2.5781 | 4 | 4
PBB | 0.58382 | ESB | ROI | GU_400325 | PBB | Poolbeg C_B |  | Gas | 1 |  |  | Gas | 120 | 256 |  | 46.88% | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 6.2% | 154 | 11 | 2.5781 | 11 | 2.5781 | 4 | 4
SK3 | 0.72 | Aughinish | ROI | GU_400120 | SK3 | Sealrock 3 (Aughinish CHP) |  | Gas | 1 |  |  | Gas | 40 | 83 |  | 48.19% | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 6.2% | 44 | 6 | 4.3373 | 6 | 4.3373 | 4 | 4
SK4 | 0.72 | Aughinish | ROI | GU_400121 | SK4 | Sealrock 4 (Aughinish CHP) |  | Gas | 1 |  |  | Gas | 40 | 83 |  | 48.19% | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 6.2% | 44 | 6 | 4.3373 | 6 | 4.3373 | 4 | 4
TY | 0.67896 | Tynagh | ROI | GU_400530 | TY | Tynagh |  | Gas | 1 |  |  | Gas | 194 | 404 | 377.7 | 48.02% | 594 | 200 | 250 | 330 | 404 |  | 4.732 | 4.932 | 5.3247 | 6.2201 |  | 6.2% | 22 | 15 | 2.2277 | 12.5 | 1.8564 | 4 | 4
WG | 0.74792 | BGE | ROI | GU_400930 | WG | Whitegate |  | Gas | 1 |  |  | Gas | 180 | 445 | 432 | 40.45% | 666.68 | 185 | 399 | 460 |  |  | 3.91 | 5.265 | 5.265 |  |  | 6.2% | 32.1 | 20.6 | 2.7775 | 26.8 | 3.6135 | 4 | 4
BGT1 | 0.32579 | AES | NI | GU_500283 | BGT1 | Ballylumford GT1 |  | Gasoil | 1 |  |  | Gasoil | 8 | 58 |  | 13.79% | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2.4% | 72 | 5 | 5.1724 | 6.43 | 6.6517 | 0.02 | 0.25
BGT2 | 0.32579 | AES | NI | GU_500284 | BGT2 | Ballylumford GT2 |  | Gasoil | 1 |  |  | Gasoil | 8 | 58 |  | 13.79% | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2.4% | 72 | 5 | 5.1724 | 6.43 | 6.6517 | 0.02 | 0.25
CGT8 | 0.32579 | ESB | NI | GU_500041 | CGT8 | Coolkeeragh OCGT |  | Gasoil | 1 |  |  | Gasoil | 8 | 53 |  | 15.09% | 180 | 53 |  |  |  |  | 11.05 |  |  |  |  | 2.4% | 469 | 50 | 56.6038 | 50 | 56.6038 | 0.02 | 0.25
ED3 | 0.37895 | BnM | ROI | GU_401010 | ED3 | Cushaling |  | Gasoil | 1 |  |  | Gasoil | 20 | 58 |  | 34.48% | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5.1724 | 5 | 5.1724 |  | 0.5
ED5 | 0.37895 | BnM | ROI | GU_401011 | ED5 | Cushaling |  | Gasoil | 1 |  |  | Gasoil | 20 | 58 |  | 34.48% | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 2.4% | 24 | 5 | 5.1724 | 5 | 5.1724 |  | 0.5
AGU | 0.33561 | iPower | NI | GU_501130 | iPower AGU | iPower AGU |  | Gasoil | 1 |  |  | Gasoil |  | 64 |  | 0% | 42.943 |  | 64 |  |  |  | 10.7266 | 10.7266 |  |  |  | 2.4% | 48 | 8 | 7.5 | 8 | 7.5 | 0.5 | 0.5
KGT1 | 0.32579 | AES | NI | GU_500824 | KGT1 | Kilroot GT1 |  | Gasoil | 1 |  |  | Gasoil | 5 | 29 |  | 17.24% | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2.4% | 24 | 2.67 | 5.5241 | 2.67 | 5.5241 | 0.02 | 0.25
KGT2 | 0.32579 | AES | NI | GU_500825 | KGT2 | Kilroot GT2 |  | Gasoil | 1 |  |  | Gasoil | 5 | 29 |  | 17.24% | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 2.4% | 24 | 2.67 | 5.5241 | 2.67 | 5.5241 | 0.02 | 0.25
KGT3 | 0.3898 | AES | NI | GU_500820 | KGT3 | Kilroot GT3 |  | Gasoil | 1 |  |  | Gasoil | 12.8194 | 42 |  | 30.52% | 115.3926 | 12.8194 | 41.6075 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2.4% | 24 | 10 | 14.2857 | 10 | 14.2857 | 0.62 | 0.38
KGT4 | 0.3898 | AES | NI | GU_500821 | KGT4 | Kilroot GT4 |  | Gasoil | 1 |  |  | Gasoil | 12.8194 | 42 |  | 30.52% | 115.3926 | 12.8194 | 41.6075 |  |  |  | 9.2356 | 9.2356 |  |  |  | 2.4% | 24 | 10 | 14.2857 | 10 | 14.2857 | 0.62 | 0.38
RH1 | 0.3665 | SSE | ROI | GU_400770 | RH1 | Rhode 1 |  | Gasoil | 1 |  |  | Gasoil | 5 | 52 |  | 9.615% | 85.01 | 12 | 52 |  |  |  | 9.8226 | 9.8226 |  |  |  | 2.4% | 50 | 10 | 11.5385 | 10 | 11.5385 |  | 0.75
RH2 | 0.3665 | SSE | ROI | GU_400771 | RH2 | Rhode 2 |  | Gasoil | 1 |  |  | Gasoil | 5 | 52 |  | 9.615% | 85.01 | 12 | 52 |  |  |  | 9.8226 | 9.8226 |  |  |  | 2.4% | 50 | 10 | 11.5385 | 10 | 11.5385 |  | 0.75
TP1 | 0.37552 | SSE | ROI | GU_400780 | TP1 | Tawnaghmore 1 |  | Gasoil | 1 |  |  | Gasoil | 5 | 52 |  | 9.615% | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 2.4% | 50 | 10 | 11.5385 | 10 | 11.5385 |  | 0.75
TP3 | 0.37552 | SSE | ROI | GU_400781 | TP3 | Tawnaghmore 3 |  | Gasoil | 1 |  |  | Gasoil | 5 | 52 |  | 9.615% | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 2.4% | 50 | 10 | 11.5385 | 10 | 11.5385 |  | 0.75
TB1 | 0.30848 | SSE | ROI | GU_400750 | TB1 | Tarbert Unit 1 |  | Oil | 0.61 | Gasoil | 0.39 | Oil | 18 | 54 |  | 33.33% | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 2% | 50 | 1 | 1.1111 | 1 | 1.1111 | 2 | 2
TB2 | 0.30848 | SSE | ROI | GU_400751 | TB2 | Tarbert Unit 2 |  | Oil | 0.61 | Gasoil | 0.39 | Oil | 18 | 54 |  | 33.33% | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 2% | 50 | 1 | 1.1111 | 1 | 1.1111 | 2 | 2
TB3 | 0.41914 | SSE | ROI | GU_400752 | TB3 | Tarbert Unit 3 |  | Oil | 0.7 | Gasoil | 0.3 | Oil | 34.85 | 243 |  | 14.34% | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.0698 | 8.0698 | 9.063 | 9.153 |  | 2% | 50 | 2 | 0.49383 | 2.2 | 0.54321 | 4 | 4
TB4 | 0.40147 | SSE | ROI | GU_400753 | TB4 | Tarbert Unit 4 |  | Oil | 0.7 | Gasoil | 0.3 | Oil | 34.85 | 243 |  | 14.34% | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.4 | 8.4 | 9.428 | 9.64 |  | 2% | 50 | 2 | 0.49383 | 2.2 | 0.54321 | 4 | 4
ED1 | 0.49466 | BnM | ROI | GU_401860 | ED1 | Edenderry |  | Gasoil | 1 |  |  | Peat | 41 | 117.6 |  | 34.86% | 497.6 | 88 | 112 | 118 |  |  | 3.933 | 8.95 | 8.95 |  |  | 7.9% | 72 | 1.76 | 0.89796 | 1.76 | 0.89796 | 4 | 0.5
LR4 | 0.40858 | ESB | ROI | GU_400240 | LR4 | Lough Ree |  | Peat | 1 |  |  | Peat | 91 | 93 |  | 97.85% | 86.8 | 91 | 93 |  |  |  | 8.811 | 8.811 |  |  |  | 7.9% | 339 | 0.5 | 0.32258 | 0.5 | 0.32258 | 4 | 4
WO4 | 0.41575 | ESB | ROI | GU_400370 | WO4 | West Offaly |  | Peat | 1 |  |  | Peat | 137 | 140 |  | 97.86% | 120.5 | 137 | 140 |  |  |  | 8.659 | 8.659 |  |  |  | 7.9% | 339 | 0.7 | 0.3 | 0.7 | 0.3 | 4 | 4
DBW | 1 | Covanta | ROI | GU_402030 | Dublin | Dublin Waste to Energy |  | Gasoil | 1 |  |  | Waste | 21.35 | 68.197 |  | 31.31% | [11 empty] | 6.7% | 36 | 5 | 4.399 | 5 | 4.399
IW1 | 1 | Indaver | ROI | GU_401230 | IW1 | Meath waste to energy | [5 empty] | Waste | 1 | 17 |  | 5.882% | [11 empty] | 6.7% | 2.3 | 0.36 | 1.2706 | 0.65 | 2.2941
Lisahally | 0.4 | Maydown | NI | GU_501350 | Lisahally | Maydown |  | Oil | 1 |  |  | Waste wood | 12.74 | 17.6 |  | 72.39% | 40 | 17.6 |  |  |  |  | 9 |  |  |  |  | 6.7% | 24 | 0.04 | 0.13636 | 0.04 | 0.13636 | 4 | 0.5